## Overview
OVERVIEW |  | Data Center IT Equipment Assessment Tool, Version 2.5, October 27, 2023
This tool was developed by Lawrence Berkeley National Laboratory (LBNL) for the US Department of Energy (DOE)
Copyright© 2023 The Regents of the University of California, operator of the Lawrence Berkeley National Laboratory. All Rights Reserved.
Screen (tab) | Description |  | What does this Tool do?
IT equipment is at the core of energy consumption in data centers. Energy savings at the IT
Overview | This Sheet: Provides an overview of data flow and screen descriptions. |  | level will have an impact on essentially all energy use in data centers. Based on user input,
this Tool estimates overall energy savings by a number of saving measures. It is designed to
Inventory | User input: Collects the IT inventory and assigned Classes. |  | help identify areas for energy savings improvements.
Classes 1-4 | User input: Collects Class specific energy savings measures. |  | How is the Tool used?
First, the user fills in data and answers questions on up to six input screens. Each
Questions | User input: Questions for crafting hands-on recommendations. |  | screen includes basic guidance for entering the data correctly. Second, based on this user
input, numerical output and recommended actions are given on two result output screens.
Numerical Results | Result output: Provides calculated numerical results.
Tool suite
Recommendations | Result output: Provides hands-on recommendations. |  | This IT Equipment Tool is part of a tool suite, which includes HVAC, electrical, and IT tools.
Currently, the individual tools are designed as "stand-alone" modules. More information
at http://datacenters.lbl.gov/tools
Questions, comments, and/or suggestions?
Please contact mkherrlin@lbl.gov

## Inventory
Inventory
This screen allows the user to create an inventory of the IT equipment, and group
the equipment into four user-defined Classes.
[5 empty] | Table 2a: IT Equipment Inventory | [6 empty] | Table 2b: Utilization
First, provide a description of each "IT Equipment Class" and assign a Power Performance
level (Table 1). A unique set of energy saving measures will be applied to each Class | [5 empty] | IT Equip | Number | Actual | Max | IT Equip |  | Power | Comp |  |  |  |  | Actual |  |  |  | Max
on the next four screens (tabs). |  |  |  |  | # | Type | of Units | Power [W] | Power [W] | Class | ERROR Messages | Util. [%] | Util. [%] |  | Potential Actions |  |  | C1 | C2 | C3 | C4 | C1 | C2 | C3 | C4
[5 empty] | 1 | A | 20 | 350 | 700 | 1 |  | 50 | 48.453 | High |  | Consolidate |  | 7000 | 0 | 0 | 0 | 14000 | 0 | 0 | 0
Second, each Class is populated with IT equipment (Table 2a). An "IT Equipment Type" is |  |  |  |  | 2 | B | 4 | 400 | 500 | 4 |  | 80 | 79.184 | Mid |  |  |  | 0 | 0 | 0 | 1600 | 0 | 0 | 0 | 2000
equipment with similar power draw. Actual and Max Power are per equipment unit. |  |  |  |  | 3 | C | 5 | 800 | 2000 | 2 |  | 40 | 33.789 | High |  | Consolidate |  | 0 | 4000 | 0 | 0 | 0 | 10000 | 0 | 0
[5 empty] | 4 | D | 1 | 1200 | 1800 | 3 |  | 66.6667 | 61.759 | Mid |  |  |  | 0 | 0 | 1200 | 0 | 0 | 0 | 1800 | 0
Third, the Tool compiles the user input into Tables 2b and 3. |  |  |  |  | 5 | E | 8 | 100 | 500 | 1 |  | 20 |  | High | Remove |  |  | 800 | 0 | 0 | 0 | 4000 | 0 | 0 | 0
[5 empty] | 6 | F | 10 | 300 | 320 | 2 |  | 93.75 | 95.4503 | High |  |  |  | 0 | 3000 | 0 | 0 | 0 | 3200 | 0 | 0
[5 empty] | 7 | G | 6 | 400 | 500 | 4 |  | 80 | 79.184 | Mid |  |  |  | 0 | 0 | 0 | 2400 | 0 | 0 | 0 | 3000
Table 1: IT Equipment Class Descriptions |  |  |  |  | 8 | H | 20 | 500 | 600 | 3 |  | 83.3333 | 83.0652 | Mid |  |  |  | 0 | 0 | 10000 | 0 | 0 | 0 | 12000 | 0
[5 empty] | 9 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IT Equip | Description |  |  | Power | 10 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Class |  |  |  | Performance | 11 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Class 1 | X Servers |  |  | High | 12 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Class 2 | Y Servers |  |  | High | 13 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Class 3 | Z Servers |  |  | Mid | 14 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Class 4 | Mixed Servers |  |  | Mid | 15 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 16 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 17 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 18 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Table 3: IT Equipment Inventory by Class and total |  |  |  |  | 19 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 20 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IT Equip | Actual | Max | Power |  | 21 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Class | Power | Power | Util [%] |  | 22 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Class 1 | 7800 | 18000 | 43.3333 |  | 23 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Class 2 | 7000 | 13200 | 53.0303 |  | 24 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Class 3 | 11200 | 13800 | 81.1594 |  | 25 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Class 4 | 4000 | 5000 | 80 |  | 26 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sum | 30000 | 50000 | 60 |  | 27 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 28 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ERROR Messages |  |  |  | 29 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 30 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 31 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 32 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 33 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 34 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 35 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 36 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 37 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 38 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 39 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 40 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 41 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 42 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 43 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 44 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 45 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 46 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 47 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 48 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 49 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 50 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[17 empty] | Sum | 7800 | 7000 | 11200 | 4000 | 18000 | 13200 | 13800 | 5000

## Class 1
Class 1
|  | Table 4: Energy Saving Measures for IT Equipment Class 1 | [10 empty] | This screen allows the user to provide a description of changes to
IT inventory (yellow cells) for Class 1. "Current" refers to current
|  | Current Power |  |  |  | Target Power | [6 empty] | conditions and "Target" refers to the conditions after changes.
|  | Actual | Max | Power | Comp | Actual | Max | Power | Comp Util. [%] | Power Reduction | Power
|  | Power [W] | Power [W] | Util. [%] | Util. [%] | Power [W] | Power [W] | Util. [%] |  | Factor | Save [W] |  | ERROR Message #
Adding | [5 empty] | 490 | 1000 | 49 | 47.0578 |  | -490 | E12
Removing |  | 800 | 4000 | 20 | [6 empty] | 800 | E13
Replacing | [9 empty] | 0 |  | E14
Modifying | [11 empty] | Reserved for future use. |  | Power Performance
Consolidating |  | 7000 | 14000 | 50 | 48.453 | 5000 | 8000 | 62.5 | 64.6327 |  | 2000 | E15 |  | High | 3
Clouding | [11 empty] | E16
Unchanged | [11 empty] | E17 |  | High | 3
Universal | [11 empty] | E18
Total |  | 7800 | 18000 | 43.3333 | 38.8556 | 5490 | 9000 | 61 | 62.8113 |  | 2310
Table 3 Total |  | 7800 | 18000 | [6 empty] | Save Total | 2310
|  |  | Include this form? If Yes, IT Tool will check for Errors. |  |  |  |  | Yes |  | ERRORS Found
INFO and ERROR Message #
| I1 | INFO: Total Power Save ≠ Waste Recovery since IT equipment added
E1
E2
E3
E4
E5
E6
| E7 | ERROR (Multiple): Current Power Utilization must not be <26.
E8
E9
E10
E11

## Class 2
Class 2
|  | Table 5: Energy Saving Measures for IT Equipment Class 2 | [10 empty] | This screen allows the user to provide a description of changes to
IT inventory (yellow cells) for Class 2. "Current" refers to current
|  | Current Power |  |  |  | Target Power | [6 empty] | conditions and "Target" refers to the conditions after changes.
|  | Actual | Max | Power | Comp | Actual | Max | Power | Comp Util. [%] | Power Reduction | Power
|  | Power [W] | Power [W] | Util. [%] | Util. [%] | Power [W] | Power [W] | Util. [%] |  | Factor | Save [W] |  | ERROR Message #
Adding | [11 empty] | E12
Removing | [11 empty] | E13
Replacing | [9 empty] | 0 |  | E14
Modifying | [11 empty] | Reserved for future use. |  | Power Performance
Consolidating |  | 4000 | 10000 | 40 | 33.789 | 3500 | 6000 | 58.3333 | 59.4937 |  | 500 | E15 |  | High | 3
Clouding | [11 empty] | E16
Unchanged |  | 3000 | 3200 | 93.75 | 95.4503 | 3000 | 3200 | 93.75 | 95.4503 |  | 0 | E17 |  | High | 3
Universal | [11 empty] | E18
Total |  | 7000 | 13200 | 53.0303 | 52.5878 | 6500 | 9200 | 70.6522 | 73.9767 |  | 500
Table 3 Total |  | 7000 | 13200 | [6 empty] | Save Total | 500
|  |  | Include this form? If Yes, IT Tool will check for Errors. |  |  |  |  | Yes |  | No ERRORS Found
INFO and ERROR Message #
I1
E1
E2
E3
E4
E5
E6
E7
E8
E9
E10
E11

## Class 3
Class 3
|  | Table 6: Energy Saving Measures for IT Equipment Class 3 | [10 empty] | This screen allows the user to provide a description of changes to
IT inventory (yellow cells) for Class 3. "Current" refers to current
|  | Current Power |  |  |  | Target Power | [6 empty] | conditions and "Target" refers to the conditions after changes.
|  | Actual | Max | Power | Comp | Actual | Max | Power | Comp Util. [%] | Power Reduction | Power
|  | Power [W] | Power [W] | Util. [%] | Util. [%] | Power [W] | Power [W] | Util. [%] |  | Factor | Save [W] |  | ERROR Message #
Adding | [11 empty] | E12
Removing | [11 empty] | E13
Replacing |  | 10000 | 12000 | 83.3333 | 83.0652 | 5000 | 6000 | 83.3333 | 83.0652 | 0.5 | 5000 | E14
Modifying | [11 empty] | Reserved for future use. |  | Power Performance
Consolidating | [11 empty] | E15 |  | Mid | 2
Clouding | [11 empty] | E16
Unchanged |  | 1200 | 1800 | 66.6667 | 61.759 | 1200 | 1800 | 66.6667 | 61.759 |  | 0 | E17 |  | Mid | 2
Universal | [11 empty] | E18
Total |  | 11200 | 13800 | 81.1594 | 80.5548 | 6200 | 7800 | 79.4872 | 78.5705 |  | 5000
Table 3 Total |  | 11200 | 13800 | [6 empty] | Save Total | 5000
|  |  | Include this form? If Yes, IT Tool will check for Errors. |  |  |  |  | Yes |  | No ERRORS Found
INFO and ERROR Message #
I1
E1
E2
E3
E4
E5
E6
E7
E8
E9
E10
E11

## Class 4
Class 4
|  | Table 7: Energy Saving Measures for IT Equipment Class 4 | [10 empty] | This screen allows the user to provide a description of changes to
IT inventory (yellow cells) for Class 4. "Current" refers to current
|  | Current Power |  |  |  | Target Power | [6 empty] | conditions and "Target" refers to the conditions after changes.
|  | Actual | Max | Power | Comp | Actual | Max | Power | Comp Util. [%] | Power Reduction | Power
|  | Power [W] | Power [W] | Util. [%] | Util. [%] | Power [W] | Power [W] | Util. [%] |  | Factor | Save [W] |  | ERROR Message #
Adding | [11 empty] | E12
Removing | [11 empty] | E13
Replacing |  | 1600 | 2000 | 80 | 79.184 | 1200 | 1500 | 80 | 79.184 | 0.25 | 400 | E14
Modifying | [11 empty] | Reserved for future use. |  | Power Performance
Consolidating | [11 empty] | E15 |  | Mid | 2
Clouding | [11 empty] | E16
Unchanged |  | 2400 | 3000 | 80 | 79.184 | 2400 | 3000 | 80 | 79.184 |  | 0 | E17 |  | Mid | 2
Universal | [11 empty] | E18
Total |  | 4000 | 5000 | 80 | 79.184 | 3600 | 4500 | 80 | 79.184 |  | 400
Table 3 Total |  | 4000 | 5000 | [6 empty] | Save Total | 400
|  |  | Include this form? If Yes, IT Tool will check for Errors. |  |  |  |  | Yes |  | No ERRORS Found
INFO and ERROR Message #
I1
E1
E2
E3
E4
E5
E6
E7
E8
E9
E10
E11

## Questions
Questions
| # | Question | Yes/No | This screen allows the user to answer a number of IT equipment assessment questions.
| 1 | Have you defined “Critical Values” (hot-button issues that are top-of-mind of executives) for the IT project? | No | A "No" answer will result in a recommendation on the Recommendations screen (tab).
| 2 | Have you identified the organizational stakeholders for the IT project? | No | IF unsure, enter "No".
| 3 | Are you keeping an IT equipment inventory? | Yes
| 4 | Do you track IT asset utilization? | No
| 5 | Is there an Information Technology Asset Management (ITAM) system present to monitor IT utilization and status? | No
| 6 | Are unused or obsolete IT equipment systematically removed from the data center space? | Yes
| 7 | Do you require Energy Star certification on purchase of new IT equipment? | No
| 8 | Do you have a way of discerning business-application processes from overhead processes? | No
| 9 | Are you able to observe utilization of virtual assets? | No
| 10 | Is your method of tracking IT utilization able to produce reports timely to enable Operations to manage inventory? | No
| 11 | Do you have tools and processes for assessing IT asset utilization? | No
| 12 | Do you have a clear decommissioning process for IT equipment? | Yes
| 13 | Does the IT equipment refresh plan consider the age of the equipment? | Yes
| 14 | Are “80+” power supply units (PSUs) required in equipment procurement? 80+ is a specification for PSU efficiency. | No
| 15 | Have you considered the impact of your public cloud providers in your energy and carbon estimates? | No
| 16 | Are power management features enabled in IT equipment that is in service? | Yes
| 17 | Have you established an Energy Activity Policy? | No
| 18 | Does the IT Provisioning Policy include energy-related rules and conditions? | No
| 19 | Are all servers less that 4 years old? | No
| 20 | Are all servers utilized above the idling (zombie) state? | Yes
| 21 | Are all servers utilized above the under-utilized state? | No
| 22 | Is the management system capable to access onboard server sensors for key operational parameters? | No
| 23 | Are you purchasing servers accepting higher than standard intake temperatures? | No
| 24 | Have you performed a server audit to ensure all servers are still in active use? | No

## Num Results
Numerical Results
Power Utilization | Current | 60 | % |  |  |  | This screen shows the calculated results in the white boxes and "scalers" in the yellow input
| Target | 71.4426 | % |  |  |  | boxes. The latter can be changed by the user to quickly evaluate the impact on the results. | [5 empty] | List Row
1
[7 empty] | Except for the Current Power Utilization result box, all result boxes will be impacted by a Yes |  |  |  | Custom | 1.1
IT Power Savings |  | 8210 | W |  |  |  | or No answer (cell I23) on the Class screens (tabs). Please ensure the boxes are set to the |  |  |  | AL | 0.751
[7 empty] | intended value. |  |  |  | AK | 0.92
Infrastructure Power Savings |  | 4105 | W | PUE | 1.5 | [5 empty] | AZ | 0.725
[11 empty] | AR | 1.087
Total Energy Savings |  | 107879.4 | kWh/year | [7 empty] | CA | 0.479
[11 empty] | CO | 1.217
Total Energy Cost Savings |  | 12945.528 | $/year | Energy Price | 0.12 | $/kWh |  |  |  |  | CT | 0.515
[8 empty] | Select State/Custom | Custom |  | DE | 0.868
Total Carbon Savings |  | 118667.34 | lbs/year | Emission Rate | 1.1 | lbs/kWh |  |  | 1.1 | lbs/kWh | FL | 0.834
[11 empty] | GA | 0.758
Simple Payback |  | 1.9312 | years | Cost to Implement | 25000 | $ |  | T&D Losses | 0 | % | HI | 1.491
[11 empty] | ID | 0.271
Water Savings (on-site) |  | 143839.2 | L/year | WUE | 2 | L/kWh(IT) |  |  |  |  | IL | 0.653
[11 empty] | IN | 1.633
[11 empty] | IA | 0.769
Data for export to the Electrical (Power Chain) Tool or the Air Management Tool: | [10 empty] | KS | 0.838
[11 empty] | KY | 1.727
IT Power Pre-Implementation |  | 30000 | W | [7 empty] | LA | 0.826
[11 empty] | ME | 0.301
IT Power Post-Implementation |  | 21790 | W | [7 empty] | MD | 0.698
[11 empty] | MA | 0.851
[11 empty] | MI | 1.004
[11 empty] | MN | 0.826
[11 empty] | MS | 0.834
[11 empty] | MO | 1.636
[11 empty] | MT | 1.045
[11 empty] | NE | 1.125
[11 empty] | NV | 0.715
[11 empty] | NH | 0.304
[11 empty] | NJ | 0.481
[11 empty] | NM | 1.134
[11 empty] | NY | 0.455
[11 empty] | NC | 0.669
[11 empty] | ND | 1.341
[11 empty] | OH | 1.208
[11 empty] | OK | 0.754
[11 empty] | OR | 0.326
[11 empty] | PA | 0.726
[11 empty] | RI | 0.833
[11 empty] | SC | 0.567
[11 empty] | SD | 0.303
[11 empty] | TN | 0.698
[11 empty] | TX | 0.856
[11 empty] | UT | 1.561
[11 empty] | VT | 0.036
[11 empty] | VA | 0.599
[11 empty] | WA | 0.202
[11 empty] | WV | 1.944
[11 empty] | WI | 1.267
[11 empty] | WY | 1.834

## Recommendations
Recommendations
| # | Recommendation | This screen shows recommendations based on user responses on the Questions screen
| 1 | CRITICAL VALUE: Since energy savings alone are likely not an important justification for energy assessment projects, it is critical that the assessor articulates both the total value and the critical value (hot buttons) to the business. | (tab). A blank field means that the corresponding question was answered "Yes".
| 2 | STAKEHOLDERS: There are many stakeholders. The obvious ones are Facilities and IT, but that’s far from all. You have to crawl each thread of this web to identify those who may benefit from the project or potentially be harmed.
3
| 4 | UTILIZATION: Tracking IT utilization plays a central role in making the IT (and infrastructure) estate energy efficient. Methods should be in place to continuously monitor the utilization. Energy Star equipment requires direct access to CPU utilization.
| 5 | ITAM: An Information Technology Asset Management system is the best way to manage IT gear. ITAM can also be programmed to automatically alarm or report on conditions that will be favorable for waste harvesting and consolidation.
6
| 7 | ENERGY STAR: Energy Star certified IT equipment ensure certain levels of energy efficiency and control of energy-related operation. Energy Star requires direct access to power, intake temperatures, and processor utilization. Strongly recommended.
| 8 | OVERHEAD WORK: The ability to determine the level of data processing due to execution of business applications versus overhead functions can provide additional opportunities for consolidation of workloads and reducing IT gear count.
| 9 | VIRTUAL IT EQUIPMENT: IT equipment waste occurs to virtual as well as physical assets. Because of the high level of virtualization in enterprise data centers, it is necessary to apply the same analytical rigor to virtual assets.
| 10 | UTILIZATION TRACKING: In absence of an Information Technology Asset Management (ITAM) system, it may be necessary to schedule (and budget) for routine recurring IT audits. Audits should be designed to identify unused or underutilized equipment.
| 11 | UTILIZATION TOOLS: The assessor should establish an inventory of tools and the Methods of Procedure (MOPs) to assess asset utilization. This inventory of tools and processes can also serve as a basis of justification to acquire more sophisticated tools.
12
13
| 14 | 80+ POWER SUPPLIES: 80+ power suppies can deliver savings even beyond the Energy Star requirements. There are multiple tiers and the highest tier provides around 92% energy efficiency. Strongly recommended for new equipment.
| 15 | CLOUD WORKLOADS: Transferring workload to the cloud is likely to reduce total energy and carbon, but does not eliminate them for that workload. Declare a method of estimation for the impact of outsourcing those workloads to cloud operators.
16
| 17 | ENERGY ACTIVITY POLICY: The Energy Activity Policy, as a part of the SLA, provides the operational framework for balancing energy consumption with availability and performance requirements.
| 18 | PROVISIONING POLICY: Provisioning reviews should be regular and periodic to reflect utilization, SLA’s, and technology changes. Since new equipment process data more energy efficiently this has to be taken into consideration in the provisioning policy.
| 19 | REFRESH: Consider a server refresh. Servers are cost effective for 3-5 years. New servers have higher processing power with smaller footprint. They also have better energy characteristics and energy management features making them more energy efficient.
20
| 21 | CONSOLIDATION: Under-utilized servers should be consolidated. A server at 10-50% utilization may be a candidate. Virtualization is an example of a software-based consolidation technology. Consolidation results in space and energy savings.
| 22 | ONBOARD SENSORS: Accessing onboard server sensors (rather than relying on external sensors) for key operational parameters is cost effective and makes server management much easier. Onboard sensors are always an integral part of the server itself.
| 23 | INTAKE AIR TEMPERATURES: Purchasing servers accepting higher intake temperatures will help the overall efforts to save energy in data centers. Allowing higher intake air temperature results in energy savings in the data center cooling system.
| 24 | SERVER AUDITS: Server audits identify non-active servers and help establish an action plan for effective server management, including equipment decommissioning and consolidation efforts.