## FacilityOverview
Facility Overview
Prioritize metrics and data collection to capture a high-level description of the facility.
Paste information from the Site Description Survey, Energy Management Practices Survey, and/or one of the DC Pro Tools. See links for further guidance:
Energy Assessment Process Manual
DC Pro Tools
Recommended Metrics
Metric | Unit/Value/Notes
Embedded in a larger building or standalone?
Current usage factor (% of space)
Year built
IT equipment layout (hot-aisle/cold-aisle arrangement, UPSs and PDUs present?)
Basic description of cooling equipment (CRAHs or CRACs?)
Any other noteworthy characteristics
Recommended Data Collection
Data Required for Metrics | Unit | Priority | Value | Measurement/Calculation Approach | Responsible Party | CoE Guidance
Data Center Floor Area (Electrically Active Floor Area) | sf
Data Center Gross Area | sf
Source Energy Factors | [5 empty] | Use local source factors if available, else national averages
Outside Dry Bulb Temperature | °F |  |  |  |  | Needed for HVAC analysis/diagnostics
Outside Wet Bulb Temperature | °F |  |  |  |  | Needed for HVAC analysis/diagnostics
List of Abbreviations
AC – Alternating Current
ASHRAE – American Society of Heating, Refrigerating, and Air-Conditioning Engineers
BTU/sf-y – British Thermal Units per square foot per year
CFM – Cubic Feet per minute
CRAC – Computer Room Air-Conditioner (with internal refrigerant compressor)
CRAH – Computer Room Air Handler (with chilled water coil)
DC – Data Center
EEM – Energy Efficiency Measure
ECM – Electronically Commutated Motor
°F – degree(s) Fahrenheit
GWh/yr – GigaWatt Hours per year (millions of kWh/yr)
HVAC – Heating, Ventilating, and Air-Conditioning
IT – Information Technology
kV – kiloVolts (thousands of volts of electrical potential)
kVA - kiloVolt-Amperes of apparent power
kW – kiloWatts of real power
kWh – kiloWatt hour
NPLV – Non-standard Part-Load Value
PDU – Power Distribution Unit
PUE – Power Usage Effectiveness
RCI – Rack Cooling Index
RTI – Return Temperature Index
RH – Relative Humidity
sf – square foot
TAB – Test, Adjust, and Balance
TCO – Total Cost of Ownership
UPS – Uninterruptible Power Supply
V – Volt(s)
VFD – Variable Frequency Drive (for operating motors at variable speed)
W/cfm – Watts (of electrical power input) per cubic feet per minute (of air flow)
W/gpm - Watts (of electrical power input) per gallon per minute (of water flow)
W/sf – watts per square foot

## FacilityEnergyUse
Facility Energy Use
Prioritize metrics and data collection to capture energy use and IT equipment loads
Edit the end-use categories and data to the data center currently being assessed to calculate PUE and populate the charts
Data Center Metering and Resource Guide
Recommended Metrics
Metric | Unit | Data Required | Priority | CoE Guidance | Value | Notes
Average Load | kW
Yearly energy use | MWh/yr
Data center separately sub-metered? | Yes
No
Current usage factor (% of space) | %
PUE (Total Power/IT Power) |  | IT Peak Power and Total DC (Data Center) Peak Elec Demand - see table and chart below
HVAC Effectiveness (IT Power /HVAC Power) |  | IT Peak Power and Total DC HVAC Peak Power
Site Energy Use Intensity | Site BTU/sf-yr | Total DC Energy Use (Site) and DC Floor Area
Source Energy Use Intensity | Source BTU/sf-yr | Total DC Energy Use (Source) and DC Floor Area
Purchased Energy Cost Intensity | Energy $/sf-yr | Total DC Energy Cost and DC Floor Area
Peak Electrical Demand Intensity | Peak W/sf | Total DC Peak Elec Demand and DC Floor Area
Description of how energy use was estimated (e.g., a combination of temporary sub-metering, equipment energy use estimates, spot measurements, and spreadsheet calculations)
Recommended Data Collection
Data Required for Metrics | Unit | Priority | Value | Measurement/Calculation Approach | Responsible Party | CoE Guidance
Data Center Floor Area (Electrically Active Floor Area) | sf
IT Peak Power | kW
Total DC (Data Center) Energy Use (Site) | kBTU
Total DC Energy Use (Source) | kBTU
Total DC Electrical Energy Use | kWh
Total DC Fuel Energy Use | MMBTU
Total DC Purchased Chilled Water Use | MMBTU
Total DC Purchased Steam Use | MMBTU
Total DC Purchased Energy Cost | $
Total DC Peak Electrical Demand | kW
Total DC HVAC Peak Power | kW
IT Equipment Loads
Data Center Areas | Area (sf) | IT equipment load (kW) | Power Density (W/sf) | Date | Notes
Total | 0 | 0 | 0
Current Energy Use Breakdown (sample values provided)
End Use | Percentage of Data Center Total (%) | Average Load (kW) | Date | Notes
IT equipment | 38.05% | 540
CRAH humidity control | 18.25% | 259
CRAH fans | 12.26% | 174
Cooling towers | 1.409% | 20
Condenser water pumps | 2.255% | 32
Chilled water pumps | 1.903% | 27
Chillers | 17.27% | 245
Lighting | 0.8457% | 12
Generator Standby Loss | 0.7047% | 10
UPS loss | 5.356% | 76
Transformer and PDU loss | 1.691% | 24
Total | 100% | 1419
PUE (Total Energy Use / IT Energy Use) | 2.6278 | 2.6278
Projected Energy Use Breakdown (sample values provided)
End Use | Percentage of Data Center Total (%) | Average Load (kW) | Date | Notes
IT equipment | 43.81% | 616
CRAH humidity control | 16.43% | 231
CRAH fans | 12.02% | 169
Cooling towers | 1.422% | 20
Condenser water pumps | 2.276% | 32
Chilled water pumps | 1.636% | 23
Chillers | 16.93% | 238
Lighting | 0.8535% | 12
Generator Standby Loss | 0.569% | 8
UPS loss | 2.703% | 38
Transformer and PDU loss | 1.351% | 19
Total | 100% | 1406
PUE (Total Energy Use / IT Energy Use) | 2.2825 | 2.2825

## CoolingSystem
Cooling System
Prioritize metrics and data collection to capture detailed information on cooling system equipment
To calculate air management metrics, it is highly recommended to use the Air Management Tool
If chilled water is supplied to units from central chilled-water plant, see ChillerPlant tab
Data Center Metering and Resource Guide
Air Management Tool
Overview (including quantity of each type of cooling equipment)
CRAC/CRAH/AHU Units
Type | Size (tons) | Manufacturer | Model # | Serial # | Notes
Recommended Metrics
Metric | Unit | Data Required | Priority | CoE Guidance | Value | Notes
CRAC/CRAH/AHU Temperature Differential | °F | Average Supply Air Temperature and Average Return Air Temperature
Average Rack Temperature Rise | °F | Rack Intake Temps and Rack Exhaust Temps
Return Temperature Index (RTI), measure of by-pass air and recirculation air | % | Average Supply Air Temperature, Average Return Air Temperature, and Average Rack Temp Rise
Rack Intake Temperatures (average) | °F | Rack Intake Temperatures
Airflow Efficiency | W/cfm | CRAC Power / AHU Power and CRAC Airflow / AHU Airflow
Ratio of Total System/CRAH Flow to Total Rack Flow | None | Total System Airflow and Total Rack Airflow
CRAC/CRAH/AHU Moisture Differential | lbs of moisture per lb of air | Entering Absolute Humidity and Leaving Absolute Humidity
Fan motor efficiency | % | Fan Motor Efficiency (Nameplate)
Economizer Utilization Factor | % | Cooling Load Served w/ Economizer and Total Cooling Load Served
Rack Cooling Index-High (RCIHI), measure of conformance with ASHRAE recommended intake temperature specification, high end of temperature range | % | Rack Intake Temperatures, Recommended Temp Range, and Allowable High Temp |  | Estimated through the Air Management Tool
Rack Cooling Index-Low (RCILO), measure of conformance with ASHRAE recommended intake temperature specification, low end of temperature range | % | Rack Intake Temperatures, Recommended Temp Range, and Allowable Low Temp |  | Estimated through the Air Management Tool
Average Heat Density (elec active) | W/sqft | Average electric power, Data Center square footage |  |  |  | Based on IT Equipment Energy Use and Data Center Floor Area (Electrically Active Floor Area)
Maximum Heat Density (elec active) | W/sqft | Maximum electric power, Data Center square footage |  |  |  | Based on IT Peak Power and Data Center Floor Area (Electrically Active Floor Area)
Total AHU Airflow | cfm |  |  | Estimated through the Air Management Tool
Max-Min AHU supply temperature | °F |  |  | Estimated through the Air Management Tool
Typical (airflow weighted) AHU supply air temperature | °F |  |  | Estimated through the Air Management Tool
Typical (airflow weighted) AHU temperature drop | °F |  |  | Estimated through the Air Management Tool
AH Cooling | kW |  |  | Estimated through the Air Management Tool
Typical (airflow weighted) equipment temperature rise | °F |  |  | Estimated through the Air Management Tool
Total IT Equipment Airflow | cfm |  |  | Estimated through the Air Management Tool
Equipment Power (=AHU cooling) | kW |  |  | Estimated through the Air Management Tool
Total Measured Power (similar DT(P) option only | kW |  |  | Estimated through the Air Management Tool
Intake Temperature Plot |  |  |  | Estimated through the Air Management Tool
Recommended Data Collection
Data Required for Metrics | Unit | Priority | Value | Measurement/Calculation Approach | Responsible Party | CoE Guidance
Actual Intake Temperature Range | °F |  |  |  |  | Representative sample (measured values)
Actual Intake Humidity Range | % RH |  |  |  |  | Representative sample (measured values)
| °F DP |  |  |  |  | Dew Point
Recommended Temp Ranges | °F |  |  |  |  | Obtain from company standard
Allowable Temp Ranges | °F |  |  |  |  | Obtain from company standard
Floor Plenum Static Pressure | in of water |  |  |  |  | Representative sample (measured values)
Floor Leakage | % |  |  |  |  | Base on total rack flow and total system flow
CRAC Power | kW
CRAC Airflow | cfm |  |  |  |  | Use TAB report or design data if measured airflow unavailable
Entering Absolute Humidity | °F DP |  |  |  |  | Dew Point
Leaving Absolute Humidity | °F DP |  |  |  |  | Dew Point
Average Electric Power (elec active) | W |  |  |  |  | IT, HVAC, and power distribution load in electrically active areas
Maximum Electric Power (elec active) | W |  |  |  |  | IT, HVAC, and power distribution load in electrically active areas
Square footage (elec active) | sqft |  |  |  |  | Data Center square footage of electrically active area
Average Rack Temperature Rise | °F |  |  |  |  | Representative sample (measured values)
Rack Intake Temperatures | °F |  |  |  |  | Representative sample (measured values). Use the AVERAGE temperature of the air entering the IT equipment, from a variety of locations in the data center. Include equipment at the bottom of racks, mid-height of racks, AND the top of racks.
Rack Exhaust Temperatures | °F |  |  |  |  | Representative sample (measured values). Use the AVERAGE temperature of the air leaving the IT equipment, from a variety of locations in the data center. Include equipment at the bottom of racks, mid-height of racks, AND the top of racks.
Average Supply Air Temperature Setpoint (if applicable) | °F |  |  |  |  | Setpoints
Average Supply Air Temperature | °F |  |  |  |  | Measured values, not setpoints. Input for Air Management Tool
Average Supply Air Humidity Setpoint (if applicable) | % RH |  |  |  |  | Setpoints
°F DP
Average Supply Air Humidity Setpoint Deadband (if applicable) | % RH |  |  |  |  | Setpoints
Minimum | °F DP
Maximum | % RH
°F DP
Average Supply Air Humidity | % RH |  |  |  |  | Measured values, not setpoints
°F DP
Average Return Air Temperature Setpoint (if applicable) | °F |  |  |  |  | Setpoints
Average Return Air Temperature | °F |  |  |  |  | Measured values, not setpoints. Choose units from different locations in the data center space. The supply temperature fluctuates greatly in some cooling units, so obtain a time-average reading that accounts for the fluctuations. Input for Air Management Tool
Average Return Air Humidity Setpoint (if applicable) | % RH |  |  |  |  | Setpoints
°F DP
Average Return Air Humidity Setpoint Deadband | % RH |  |  |  |  | Setpoints
Minimum | °F DP
Maximum | % RH
°F DP
Average Return Air Humidity | % RH |  |  |  |  | Measured values, not setpoints
°F DP
Sensor Calibration (modifiable slope & offset?) | Yes |  |  |  |  | Seldom easily available.
No
CRAC Energy Use | kWh |  |  |  |  | For end use analysis
AHU Power | kW
AHU Airflow | cfm |  |  |  |  | Use TAB report or design data if measured airflow unavailable
Total system airflow | cfm
Total rack airflow | cfm |  |  |  |  | Estimate from temp differential and power
Ratio total system flow to total rack flow | None |  |  |  |  | Use the previous two rows
Supply-side Pressure Drop | in. w.g.
Return-side Pressure Drop | in. w.g.
Fan Motor Efficiency (Nameplate) | % |  |  |  |  | Input for Air Management Tool
Air Handler Energy Use | kWh |  |  |  |  | Needed for end use analysis. Input for Air Management Tool.
AHU Airflow | cfm |  |  |  |  | Input for Air Management Tool
Measured Temperature Rise arranged in classes (DT) | °F |  |  |  |  | Input for Air Management Tool
Number of units (U) | # |  |  |  |  | Input for Air Management Tool
Measured Temperature Rise (DT) | °F |  |  |  |  | Input for Air Management Tool
Measured Power (P) | W |  |  |  |  | Input for Air Management Tool
Intake Temperature | °F |  |  |  |  | Input for Air Management Tool

## ChillerPlant
Chiller Plant
Prioritize metrics and data collection to capture detailed information on the chiller plant
Chillers and economizer heat exchangers
Manufacturer | Model # | Serial # | Size (tons) | Date | Notes
Recommended Metrics
Metric | Unit | Data Required | Priority | CoE Guidance | Value | Notes
Chiller Plant Wire to Water Efficiency | kW/ton | Total Cooling Load Served and Total Chiller Plant Energy Use
Chiller Rated Efficiency at Design | kW/ton NPLV | Chiller Rated Efficiency
Cooling Tower Design Efficiency | gpm/HP | Cooling Tower Energy Use and Total Cooling Load Served |  |  |  | Normally taken at CTI standard conditions of 95°F entering water, 85°F leaving water, and 78°F wet bulb temperature.
Cooling Tower Design Approach | °F | Condenser Water Supply Temp and Outside Wet Bulb Temp
Condenser Approach Temperature | °F | Condenser Refrigerant Temp and Condenser Water Return Temp
Chilled Water Pumping Efficiency | W/gpm | Chilled Water Pumps Power Chilled Water Flow
Condenser Water Pumping Efficiency | W/gpm | Condenser Water Pumps Power and Condenser Water Flow
Pump and fan motor efficiency (nameplate) | % | Pump and Fan Efficiency (Nameplate)
Water-Side Economizer Utilization Factor | % | Cooling Load Served w/ Water Econ Total Cooling Load Served
Recommended Data Collection
Data Required for Metrics | Unit | Priority | Value | Measurement/Calculation Approach | Responsible Party | CoE Guidance
Total Cooling Load Served (Annual) | Ton-Hrs |  |  |  |  | Calculated from chilled water temperature and flow measurements
Cooling Load Served w/ Water Econ (Annual) | Ton-Hrs |  |  |  |  | Load served when water economizer was on and compressors were off
Cooling Load Served w/ Econ (Annual) | Ton-Hrs |  |  |  |  | Load served when air economizer was on and compressors were off
Total Chiller Plant Energy Use (Annual) | kWh |  |  |  |  | Directly measured or calculated as sum of chiller, cooling tower, pumps
Chiller Rated Efficiency | kW/Ton |  |  |  |  | Use NPLV rating if available, then IPLV if available, then design kW/ton, then kW/ton per AHRI standard conditions. Specify which is listed.
Pump Motor Efficiency (nameplate) | %
Fan Motor Efficiency (nameplate) | %
Chilled Water Pumps Power | kW
Chilled Water Flow | gpm
Chilled Water Supply Temperature | °F
Chilled Water Return Temperature | °F
Chilled Water Pump Head | ft |  |  |  |  | May be useful for pump diagnostics
Cooling Tower Energy Use | kWh
Condenser Water Pump Power | kW
Condenser Water Flow | gpm
Condenser Water Supply Temperature | °F
Condenser Refrigerant Temperature | °F
Condenser Water Return Temperature | °F
Condenser Water Pump Head- Design | ft |  |  |  |  | May be useful for pump diagnostics
Condenser Water Pump Head- Actual | ft |  |  |  |  | May be useful for pump diagnostics
Cooling Plant Design Load | Tons |  |  |  |  | May be useful for rightsizing diagnostics
Cooling Plant Energy Use | kWh |  |  |  |  | Needed for end use analysis

## ElectricalSystem
Electrical System
Prioritize metrics and data collection to capture detailed information on the electrical system
Data Center Metering and Resource Guide
Utility Feed and General Description
UPS System Overview (e.g., count of different types, aggregated information)
UPS Units
Manufacturer | Model # | Serial # | Description (including kVA) | Topology (e.g., double-conversion?) | Meters present & working? | Notes
PDUs Overview e.g., count of different types, aggregated information)
Distribution Transformers/PDUs
Manufacturer | Model # | Serial # | Description (including kVA) | Topology (e.g., double-conversion?) | Meters present & working? | Notes
Recommended Metrics
Metric | Unit | Data Required | Priority | CoE Guidance | Value | Notes
UPS Load Factor |  | UPS Input kW and UPS rating
Measured IT Load Density | [5 empty] | If a one-time measurement, it's a spot value.
IT Average Power Density | [5 empty] | Over some period
UPS System Efficiency | % | UPS Output kW and UPS Input kW
Transformer Efficiency (upstream UPS system) Efficiency | % | XFMR Transformer Output and XFMR Transformer Input
PDU (with built-in transformer) System Efficiency | % | PDU Output and PDU Input
IT Peak Power Density | W/sf | IT Peak Power and DC Floor Area
IT Ave Power Density | W/sf | IT Avg Power and DC Floor Area
IT Peak Power Density (design) | W/sf | IT Peak Power (design) and DC Floor Area
IT Rack Power Density | kW/rack | IT Peak Power and Rack quantity
IT Rack Power Density (design) | kW/rack | IT Peak Power (design) and Rack quantity
UPS output voltage | V -120/208/480 / direct current | UPS Output voltage
Stand-by Gen Block heater power | W | Block Heater Power
Average Lighting Power Density | W/sf | DC Average Lighting Power and DC Floor Area
Lighting Overview (e.g., count of different types, controls, any other relevant information)
Recommended Data Collection
Data Required for Metrics | Unit | Priority | Value | Measurement/Calculation Approach | Responsible Party | CoE Guidance
IT Equipment Energy Use | kWh
IT Peak Power | kW
IT Peak Power (Design) | kW
IT Avg Power | kW
Rack Quantity | #
Losses | KW
Efficiency | %
UPS Input | kW
UPS Output | kW
UPS Rating | kVA / kW
UPS Input current THD | THD %
UPS Input Power factor | PF
UPS Output Voltage | V
XFMR Transformer input | kW |  |  |  |  | upstream of the UPS
XFMR Transformer output | kW |  |  |  |  | upstream of the UPS
Transformer rating | kVA
PDU Input | kW |  |  |  |  | Transformer w/in PDU (if any)
PDU Output | kW |  |  |  |  | Transformer w/in PDU (if any)
PDU Rating | kVA
Static Transfer Switch (STS) input | kW |  |  |  |  | Only if metered
Static Transfer Switch (STS) output | kW |  |  |  |  | Only if metered
Static Transfer Switch (STS) rating | A |  |  |  |  | Maybe useful for efficiency diagnostics
Generator radiator above ambient temperature?
Standby Generator block heater | kW
Standby Generator Rating | kVA / kW
Generator heater setpoint temperature
Standby Generator Ambient Temperature | °F |  |  |  |  | Maybe useful for efficiency diagnostics
Data Center Average Lighting Power | kW |  |  |  |  | Not installed, actually used
Data Center Lighting Installed Power | kW
Lighting Energy Use | kWh |  |  |  |  | Needed for end use analysis

## Summary
Summary Table of Savings
DC Pro's tailored recommendations and the Master List provide guidance on selecting/prioritizing the Recommended Energy Efficiency Measures
Data Center Master List of Energy Efficiency Actions
Saving and Payback Summary
Grouped Efficiency Measures (EEMs) | Estimated Installed Cost ($) | Estimated Yearly Energy Savings (kWh) | Estimated Yearly Dollar Savings ($) | Estimated Simple Payback (Years)
Total |  | 0 |  | #DIV/0!
Baseline and Other Notes
EEM 1
Name | Estimated Installed Cost ($) | Estimated Yearly Energy Savings (kWh) | Estimated Yearly Dollar Savings ($) | Estimated Simple Payback (Years)
Description
EEM 2
Name | Estimated Installed Cost ($) | Estimated Yearly Energy Savings (kWh) | Estimated Yearly Dollar Savings ($) | Estimated Simple Payback (Years)
Description
EEM 3
Name | Estimated Installed Cost ($) | Estimated Yearly Energy Savings (kWh) | Estimated Yearly Dollar Savings ($) | Estimated Simple Payback (Years)
Description
EEM 4
Name | Estimated Installed Cost ($) | Estimated Yearly Energy Savings (kWh) | Estimated Yearly Dollar Savings ($) | Estimated Simple Payback (Years)
Description
EEM 5
Name | Estimated Installed Cost ($) | Estimated Yearly Energy Savings (kWh) | Estimated Yearly Dollar Savings ($) | Estimated Simple Payback (Years)
Description