## Overview
Data Center Electrical Power Chain Assessment Tool
Version 2.3
12-03-2021
Lawrence Berkeley National Laboratory (LBNL) and EYP Mission Critical Facilities originally developed this tool for the U.S. Department of Energy (DOE). The developers acknowledge helpful reviews by experts from ANCIS Incorporated, Emerson, EPRI and Syska Hennessey. LBNL and Traber Engineers updated the tool in 2020. LBNL added carbon estimates in 2021.
DCEE Toolkit
This workbook is part of a tool suite for addressing energy efficiency in data centers.
The tools are available here: | https://datacenters.lbl.gov/tools
OVERVIEW
Worksheet | Description
Overview | This tab.
User Inputs A | Numeric questions about your data center's IT electric power chain and lighting systems.
User Inputs B | Multiple-choice questions about your data center's IT electric power chain and lighting systems. Suggested energy-saving actions.
Action Results | Estimated savings and simple payback for pursued actions.
Savings Summary | Estimated total savings for pursued actions.
Peer Comparison | Benchmarks for UPS load factor and IT power density.
UPS Efficiency | Lookup table for the operating efficiency of double-conversion UPSs of recent manufacture.
What does this Tool do?
This assessment tool is designed to help data center owners assess the potential energy, cost, and carbon savings from energy efficiency actions in two branches of the electrical power chain of a data center: 1. The IT branch, i.e. transformers, generators, UPSs, and PDUs. 2. The lighting system branch.
How is the Tool used?
Step 1: Answer questions and select applicable actions to pursue on the User Input A and User Input B tabs.
Step 2: Predict the post-implementation performance and the implementation cost of pursued actions on the Action Results tab.
Step 3: The Savings Summary tab presents the total predicted savings (energy, dollars, and carbon).
Step 4: The Peer Comparison tab compares some metrics of your data center to a set of other benchmarked data centers.
More Information
This tool is not a detailed "investment-grade" audit tool. The savings estimates are based on typical practice. Actual savings will vary based on site-specific conditions. This tool does not account for interactive effects among energy-saving actions, other than placing a cap on the maximum savings.
This tool presents more actions that the Electrical & Lighting sections of DC Pro (https://datacenters.lbl.gov/dcpro), but less than the Data Center Master List of Energy Efficiency Actions (https://datacenters.lbl.gov/resources/data-center-master-list-energy).
This tool presents energy-saving actions only by name. For guidance on implementing the actions, see the Master List.
This workbook contains hidden tabs that support the visible ones. To see how the workbook calculates its results, the tabs can be unhidden.

## User Inputs A
USER INPUTS: Table A
This tab accepts numeric information from the user.
Instructions
Only the green shaded cells require input.
Provide basic information about your data center by answering questions 1 through 15. The bold values refer to annual average power demand levels currently seen in your data center.
The power demand levels (kW) are converted to annual energy use (kWh/yr) in the Calculations table.
Clicking on the cells in column A3 provides pop-up guidance.
This tool does not completely safeguard against unreasonable numeric inputs.
The Calculations table shows your data center's current energy use and performance, based on your inputs.
Additional description of the tables are provided at the far right of this tab.
Calculations
Table A: Basic Information |  |  | Calc1 | Calc2 | Calc3 | Calc4 | Calc5 | Calc6 | Calc7 | Calc8 | Calc9 | Calc10 | Calc11 | Calc12 | Calc13 | Calc14
A1 | A2 | A3 | Calculations Calc5: Power Demand; Calculations Calc7: Losses; Calculations Calc10: Annual Totals; Calculations Calc12: Performance
Question Number | Question | Input | [5 empty] | Annual Average Power Demand | Annual Average Power Loss | Annual Energy Loss | Percent of Total Loss | Total Annual Energy Use | Annual Energy Cost | Nominal Capacity | Load Factor | Operating Efficiency
Q1 | What is the annual average input power of the main IT transformer in kW? | 650 | [5 empty] | kW | kW | kWh/yr | % | kWh/yr | $/yr | kW | % | %
Q2 | What is the annual average output power of the main IT transformer in kW? | 620 | Calculations Calc1: IT Systems; Calculations Calc2: IT Power Chain; Calculations Calc3: Power Transformation Equipment; Calculations Calc4: Main Transformer Serving IT Power Chain; Calculations Calc5: Input; Calculations Calc6: 650
Q3 | What is the nominal load capacity of the main IT transformer in kW? | 850 | Calculations Calc7: 30; Calculations Calc8: 262800; Calculations Calc9: 22.22%; Calculations Calc11: 39420; Calculations Calc12: 850; Calculations Calc13: 72.94%; Calculations Calc14: 95.38%
Q4 | What is the annual average input power of the UPS system in kW? | 580 | Calculations Calc5: Output; Calculations Calc6: 620
Q5 | What is the annual average output power of the UPS system in kW? | 500 | Calculations Calc4: UPS System; Calculations Calc5: Input; Calculations Calc6: 580
Q6 | What is the total load capacity of all active UPS modules in kW? | 750 | Calculations Calc7: 80; Calculations Calc8: 700800; Calculations Calc9: 59.26%; Calculations Calc11: 105120; Calculations Calc12: 750; Calculations Calc13: 66.67%; Calculations Calc14: 86.21%
Q7 | What is the UPS manufacturer's claimed efficiency at the calculated load factor shown at right? | 0% | Calculations Calc5: Output; Calculations Calc6: 500
Q8 | What is the annual average total PDU input power in kW? | 525 | Calculations Calc4: PDUs; Calculations Calc5: Input; Calculations Calc6: 525
Q9 | What is the annual average total PDU output power in kW? | 500 | Calculations Calc7: 25; Calculations Calc8: 219000; Calculations Calc9: 18.52%; Calculations Calc11: 32850; Calculations Calc12: 600; Calculations Calc13: 83.33%; Calculations Calc14: 95.24%
Q10 | What is the total load capacity of all active PDUs in kW? | 600 | Calculations Calc5: Output; Calculations Calc6: 500
Q11 | What is the annual average backup generator engine block heater power demand in kW? | 10 | Calculations Calc4: Total IT Power Chain Loss; Calculations Calc7: 135; Calculations Calc8: 1182600; Calculations Calc9: 100%; Calculations Calc11: 177390
Q12 | What is the data center floor area in sq. ft.? | 10000 | Calculations Calc3: IT Equipment; Calculations Calc6: 515; Calculations Calc10: 4511400; Calculations Calc11: 676710
Q13 | What is the annual average IT equipment power demand in kW? | 515 | Calculations Calc3: Total IT Power Chain; Calculations Calc10: 5694000; Calculations Calc11: 854100
Q14 | What is the annual average lighting power demand in kW for the data center? | 20 | Calculations Calc2: Backup Generator Engine Block Heaters; Calculations Calc6: 10; Calculations Calc10: 87600; Calculations Calc11: 13140
Q15 | What is the annual average unit cost of electricity in ¢/kWh? | 15 | Calculations Calc2: Total IT Systems; Calculations Calc10: 5781600; Calculations Calc11: 867240
|  |  | Data Center Lighting System |  |  |  |  | 20 |  |  |  | 175200 | 26280
|  |  | Totals | [8 empty] | 5956800 | 893520
Table A Description
Column
[17 empty] | A1 | Question Number | Table A contains questions number 1 through 15.
[17 empty] | A2 | Question | The text for each question is supplied by the (normally hidden) Table AA tab.
[17 empty] | A3 | Input | This column contains the user's answers to the questions. All questions require a numeric input. This tool does not completely safeguard against unreasonable inputs.
Calculations Description
Column
[17 empty] | Calc1 - Calc 4 |  | The Calculations table breaks out energy use (and energy loss) in the electric system as shown. The Main transformer, UPS System, and PDUs contribute to Total IT Power Chain Loss. This is added to IT Equipment energy use to get the Total IT Power Chain energy use. The Backup Generator Engine Block Heaters energy use is added to get the Total IT Systems energy use. Finally, the Data Center Lighting System energy use is added to get the grand total.
[17 empty] | Calc5 | Power Demand | The calculations begin by expressing everything in terms of annual average power demand. |  | This column indicates whether the power demand applies to the input side or output side of the power transformation equipment.
[17 empty] | Calc6 |  |  | Annual Average Power Demand | These values are copied from Table A.
[17 empty] | Calc7 | Losses | This section of the table calculates the power and energy loss of each of the power transformation systems. | Annual Average Power Loss | This is the difference between the input and output power demand values.
[17 empty] | Calc8 |  |  | Annual Energy Loss | This is the power loss multiplied by 8,760 hrs/yr.
[17 empty] | Calc9 |  |  | Percent of Total Loss | Each of the losses is expressed as a percent of the total loss.
[17 empty] | Calc10 | Annual Totals | This section tallies up annual energy use and annual energy cost for each element of the electric system. | Total Annual Energy Use | This is the annual average power demand multiplied by 8,760 hrs/yr.
[17 empty] | Calc11 |  |  | Annual Energy Cost | This is the annual total energy use multiplied by the annual average electric rate entered in Table A, Question 15.
[17 empty] | Calc12 | Performance | This section caluclates the performance of the power transformation equipment. | Nominal Capacity | These values are copied from Table A.
[17 empty] | Calc13 |  |  | Load Factor | This is the Output power demand divided by the Nominal Capacity.
[17 empty] | Calc14 |  |  | Operating Efficiency | This is the Output power demand divided by the Input power demand.

## User Inputs B
USER INPUTS: Table B
This tab accepts information from the user, and presents potential actions to pursue.
Instructions
Only the green shaded cells require input.
Answer questions 16 through 32 by selecting an option from the drop-down lists in column B3.
If you answer "Do not know", column B4 will suggest an evaluation to perform.
If your answer indicates the given system probably already has high efficiency, column B5 will be "No", and the potential action(s) will be "N/A".
If your answer indicates there may be room for improvement, column B5 will be "Yes", and one or more potential actions will be presented.
Column B8 provides the ability to select particular actions to pursue. If you answer "Yes" to a potential action, it will be carried over to the Action Results tab.
Additional description is provided at the bottom right of this tab.
Table B: Efficiency Information and Potential Actions
B1 | B2 | B3 | B4 | B5 | B6 | B7 | B8 | B9 | B10 | B11
Question Number | Question | Input | Evaluation to Perform if Input is "Do not know." | Is Action Recommended? | Potential Actions |  | Pursue Action? | Valid Pursuit | Answered Before Action Presented | Messages
Q16 | What is the building power factor? | Do not know. | Investigate building power factor. | Not yet | 1 | N/A | N/A | No | No
Q17 | What is the building total harmonic current distortion (THD) at main feeder panel? | Do not know. | Investigate building total harmonic current distortion (THD) at main feeder panel. | Not yet | 1 | N/A | N/A | No | No
Q18 | Are the loads balanced between all phases for the transformers, UPSs, and PDUs? | Do not know. | Determine the load balance between phases for all transformers, UPSs, and PDUs. | Not yet | 1 | N/A | N/A | No | No
Q19 | What is the age and type of the main transformer serving the IT power chain? | Do not know. | Determine the age and type of the main transformer serving the IT power chain. | Not yet | 1 | N/A | N/A | No | No
Q20 | Is there an active UPS? | Yes. |  | Yes | 1 | Shut Down UPS Modules when Redundancy Level is High Enough. | No | No | No
[5 empty] | 2 | Install a Modular UPS. | Yes | Yes | No
[5 empty] | 3 | Right-Size the UPS. | Yes | Yes | No
[5 empty] | 4 | Replace the UPS with a More Efficient Unit. | No | No | No
Q21 | Is the UPS operating in eco-mode? | Do not know. | Determine if the UPS has eco-mode capability. | Not yet | 1 | N/A | N/A | No | No
Q22 | Are the UPS DC capacitors >5 years old? | Do not know. | Determine if UPS DC capacitors are older than 5 years. | Not yet | 1 | N/A | N/A | No | No
Q23 | What is the power source for non-critical loads? | Do not know. | Investigate if non-critical loads are fed from the UPS. | Not yet | 1 | N/A | N/A | No | No
Q24 | What is the age and type of the transformers in the PDUs? | Do not know. | Determine the age and type of the transformers in the PDUs. | Not yet | 1 | N/A | N/A | No | No
Q25 | What is the average load factor for the active PDUs that contain transformers? | Do not know. | Determine the load factors for active PDUs that contain a transformer. | Not yet | 1 | N/A | N/A | No | No
Q26 | What is the IT equipment power factor? | Do not know. | Measure the IT equipment power factor. | Not yet | 1 | N/A | N/A | No | No
Q27 | What is the power source for the IT racks? | Do not know. | Investigate if IT racks are fed from an AC or DC power source. | Not yet | 1 | N/A | N/A | No | No
Q28 | What is the power source for the emergency generator block heater(s)? | Do not know. | Investigate power source for generator block heater(s). | Not yet | 1 | N/A | N/A | No | No
Q29 | Does the block heater(s)/heater water jacket for emergency generator(s) operate with thermostat control? | Do not know. | Investigate if block heater(s) operate with thermostat control. | Not yet | 1 | N/A | N/A | No | No
Q30 | Is the data center lighting well-designed? | Do not know. | Investigate the effectiveness of data center lighting. | Not yet | 1 | N/A | N/A | No | No
[5 empty] | 2 | N/A | N/A | No | No
Q31 | How are the lights controlled in the data center? | No control (always on). |  | Yes | 1 | Control Lighting with a Timeclock. | No | No | No
[5 empty] | 2 | Implement Manually Controlled Zone Lighting Control. | No | No | No
[5 empty] | 3 | Install Occupancy Sensors to Control Lights. | Yes | Yes | No
Q32 | What type of lamps are installed in the data center? | Do not know. | Investigate the type of lighting installed in th data center. | Not yet | 1 | N/A | N/A | No | No
[5 empty] | 2 | N/A | N/A | No | No
[5 empty] | 3 | N/A | N/A | No | No
Table B Description
Column
[11 empty] | B1 | Question Number | Table B contains questions number 16 through 32. Pull-down lists provide answers to select from.
[11 empty] | B2 | Question | The text for each question is supplied by the (normally hidden) Table BB tab.
[11 empty] | B3 | Input | Column B3 contains the user's answers to the questions. All of the cells in this column present a list of possible answers to select from.
[11 empty] | B4 | Evaluation to Perform if Input is "Do not know" | If the user selects "Do not know" in column B3 for any of the questions, column B4 suggests steps to take that will produce the requested information.
[11 empty] | B5 | Is Action Recommended? | Based on the user's input in column B3, column B5 will contain one of three possible phrases: "Not yet" is shown when the answer provided in column B3 is "Do not know". "Yes" is shown if the user selects an answer in column B3 that indicates there is room for an efficiency improvement. "No" is shown if the user selects an answer in column B3 that indicates that the system in question is efficient enough to not warrant potential actions.
[11 empty] | B6 | Potential Actions | The numbers in column B6 show how many potential actions this tool can suggest in response to the questions.
[11 empty] | B7 |  | If the phrase in column B5 is "Yes", then column B7 will list one or more potential energy-saving actions to take. If the phrase in column B5 is "Not yet", or "No", then column B7 will contain the phrase "N/A".
[11 empty] | B8 | Pursue Action? | For the potential actions presented in column B7, the user can indicate their intent to pursue each of them by selecting Yes, No, or N/A in column B8.
[11 empty] | B9 | Valid Pursuit | This column is normally hidden. It performs an intermediate calculation in order to simplify formulas. If column B7 is not "N/A" and column B8 is "Yes", then column B9 is "Yes", otherwise it is "No".
[11 empty] | B10 | Answered Before Action Presented | This column is normally hidden. It performs an intermediate calculation in order to simplify formulas. If column B7 is "N/A" and column B8 is not "N/A", then column B10 is "Yes", otherwise it is "No".
[11 empty] | B11 | Messages | If column B10 is "Yes", then the user is reminded that a potential action has not been presented yet. If there is a potential action presented, and the user selects "Yes" in column B8, then the action is carried over to Actions Summary tab. If the user selects "No", it is not. If two or more mutually exlusive actions are presented in column B7, and the user selects "Yes" in column B8 for more than one of them, then the user is asked to pick only one.

## Action Results
ACTION RESULTS
This tab presents the pursued actions from the User Inputs tab, asks for some additional information, and then calculates savings and simple payback.
Instructions
Only the green shaded cells require input.
Column C10 asks for the dollar cost to implement the pursued action(s).
The Savings Summary tab presents total savings.
Additional description is provided at the bottom right of this tab.
Table C: Estimated Results for Pursued Actions
C1 | C2 | C3 | C4 | C5 | C6 | C7 | C8 | C9 | C10 | C11
Question Number | Actions Pursued |  | Post-Implementation Performance |  | Estimated Savings |  |  |  | Cost to Implement | Simple Payback
[5 empty] | % | Of | kWh/yr | $/yr | $ | years
Q16 | 1 | N/A |  |  | 0 | Total IT Power Chain Loss | 0 | 0 | 0 | 0
Q17 | 1 | N/A |  |  | 0 | Total IT Power Chain Loss | 0 | 0 | 0 | 0
Q18 | 1 | N/A |  |  | 0 | Total IT Power Chain Loss | 0 | 0 | 0 | 0
Q19 | 1 | N/A |  |  | 0 | Loss in Main Transformer Serving IT Power Chain | 0 | 0 | 0 | 0
Q20 | 1 | N/A | What will the new UPS load factor be? | 80% | 77.2645 | UPS System Loss | 541469.4994 | 81220.4249 | 300000 | 3.6937
| 2 | Install a Modular UPS.
| 3 | Right-Size the UPS.
| 4 | N/A
Q21 | 1 | N/A |  |  | 0 | UPS System Loss | 0 | 0 | 0 | 0
Q22 | 1 | N/A |  |  | 0 | UPS System Loss | 0 | 0 | 0 | 0
Q23 | 1 | N/A |  |  | 0 | UPS System Loss | 0 | 0 | 0 | 0
Q24 | 1 | N/A |  |  | 0 | Total PDU Loss | 0 | 0 | 0 | 0
Q25 | 1 | N/A |  | >50% | 0 | Total PDU Loss | 0 | 0 | 0 | 0
Q26 | 1 | N/A |  |  | 0 | Total IT Equipment Energy Use | 0 | 0 | 0 | 0
Q27 | 1 | N/A |  |  | 0 | UPS System Loss | 0 | 0 | 0 | 0
Q28 | 1 | N/A |  |  | 0 | Backup Generator Engine Block Heater Total Energy Use | 0 | 0 | 0 | 0
Q29 | 1 | N/A |  |  | 0 | Backup Generator Engine Block Heater Total Energy Use | 0 | 0 | 0 | 0
Q30 | 1 | N/A |  |  | 0 | Data Center Total Lighting Energy Use | 0 | 0 | 0 | 0
| 2 | N/A
Q31 | 1 | N/A | The lights will be controlled in the data center by: | Occupancy Sensor. | 70 | Data Center Total Lighting Energy Use | 122640 | 18396 | 15000 | 0.81539
| 2 | N/A
| 3 | Install Occupancy Sensors to Control Lights.
Q32 | 1 | N/A |  |  | 0 | Data Center Total Lighting Energy Use | 0 | 0 | 0 | 0
| 2 | N/A
| 3 | N/A
Table C Description
Column
[11 empty] | C1 | Question Number |  | These question numbers reference the questions presented in Table B on the User Inputs tab.
[11 empty] | C2 | Actions Pursued |  | The numbers in column C2 show how many potential actions this tool can suggest in response to the questions.
[11 empty] | C3 |  |  | Column C3 presents the actions the user elected to pursue on the User Inputs tab.
[11 empty] | C4 | Post-Implementation Performance |  | Column C4 is similar to column B2 on the User Inputs tab, but this time it is: a) Stating the assumed post-implementation performance, or b) Asking for the predicted performance after the actions have been implemented.
[11 empty] | C5 |  |  | For the questions that have multiple post-implementation options, a pull-down list is provided.
[11 empty] | C6 | Estimated Savings | % | The values in these three columns are provided by the Table BB tab.
[11 empty] | C7 |  | Of
[11 empty] | C8 |  | kWh/yr
[11 empty] | C9 |  | $/yr
[11 empty] | C10 | Cost to Implement | $ | Enter the estimated implementation cost for the actions. If replacing equipment at end-of-life, use the cost difference between the high efficiency new equipment and the standard efficiency new equipment (assuming the former has a higher cost than the latter).
[11 empty] | C11 | Simple Payback | years | The values in this column is provided by the Table BB tab.

## Savings Summary
SAVINGS SUMMARY
Table D presents the estimated total savings (energy, cost, and carbon) for the pursued actions listed on the Action Results tab.
This workbook does not account for interactive effects between actions.
If multiple actions are selected for the UPS system or the lighting system, the workbook may accumulate unreasonably high savings percentages.
The following input fields are provided as a means of capping the total savings for those two elements of the power chain, if deemed necessary.
They can be adjusted to suit.
List Row
Cap the total UPS System Loss savings at: |  |  | 80% | [11 empty] | 1
Cap the total Data Center Lighting energy use savings at: |  |  | 80% | [9 empty] | Custom | 1.1
[13 empty] | AL | 0.782
Table D: Estimated Savings. | [12 empty] | AK | 0.97
D1 | D2 | D3 | D4 | D5 | D6 | D7 | D8 | D9 |  |  |  |  | AZ | 0.869
Item | Annual Energy Use, Pre-Implementation | Estimated Savings |  |  | Estimated Annual Energy Use, Post-Implementation | Implementation Cost | Simple Payback | Estimated Carbon (CO2) Savings |  |  |  |  | AR | 1.121
| kWh/yr | % | kWh/yr | $/yr | kWh/yr | $ | years | lbs/yr |  |  |  |  | CA | 0.386
Total IT Systems | 5781600 | 9.3654 | 541469.4994 | 81220.4249 | 5240130.5006 | 300000 | 3.6937 | 595616.4494 |  |  |  |  | CO | 1.323
Data Center Lighting System | 175200 | 70 | 122640 | 18396 | 52560 | 15000 | 0.81539 | 134904 |  |  |  |  | CT | 0.474
Total | 5956800 | 11.1488 | 664109.4994 | 99616.4249 | 5292690.5006 | 315000 | 3.1621 | 730520.4494 |  |  |  |  | DE | 0.71
[13 empty] | FL | 0.874
Table D: Estimated Savings. D3: Select State/Custom; Table D: Estimated Savings. D6: Custom | Table D Description |  |  |  | GA | 0.876
Table D: Estimated Savings. D6: 1.1; Table D: Estimated Savings. D7: [lbs/kWh] | Column |  |  |  | HI | 1.551
Table D: Estimated Savings. D3: Select State or "Custom" from the drop down menu. If "Custom" is selected, enter | D1 | Item |  | Table D summarizes the results for all IT Systems combined on the first row, the Data Center Lighting System results on the second row, and grand totals on the last row. | ID | 0.211
Table D: Estimated Savings. D3: CO2 emission rate in green box. Resulting annual emmission rate shown below. | D2 | Annual Energy Use, Pre-Implementation | kWh/yr | From column DD7 on the Table DD tab. | IL | 0.721
Table D: Estimated Savings. D5: Emission Rate:; Table D: Estimated Savings. D6: 1.1; Table D: Estimated Savings. D7: [lbs/kWh] | D3 | Estimated Savings | % | From column DD8 on the Table DD tab. | IN | 1.624
[9 empty] | D4 |  | kWh/yr | From column DD9 on the Table DD tab. | IA | 0.855
[9 empty] | D5 |  | $/yr | From column DD11 on the Table DD tab. | KS | 0.887
[9 empty] | D6 | Estimated Annual Energy Use, Post-Implementation | kWh/yr | From column DD10 on the Table DD tab. | KY | 1.768
[9 empty] | D7 | Implementation Cost | $ | From column DD12 on the Table DD tab. | LA | 0.824
[9 empty] | D8 | Simple Payback | years | From column DD13 on the Table DD tab. | ME | 0.205
[9 empty] | D9 | Estimated Carbon Savings | lbs/yr | Column D4 in Table D multiplied with the Emission Rate in Cell F24. Annual state emission rates are those published by eGRID (2021). | MD | 0.735
[13 empty] | MA | 0.773
[13 empty] | MI | 1.007
[13 empty] | MN | 0.875
[13 empty] | MS | 0.835
[13 empty] | MO | 1.587
[13 empty] | MT | 1.253
[13 empty] | NE | 1.255
[13 empty] | NV | 0.737
[13 empty] | NH | 0.251
[13 empty] | NJ | 0.543
[13 empty] | NM | 1.319
[13 empty] | NY | 0.377
[13 empty] | NC | 0.775
[13 empty] | ND | 1.436
[13 empty] | OH | 1.235
[13 empty] | OK | 0.732
[13 empty] | OR | 0.397
[13 empty] | PA | 0.755
[13 empty] | RI | 0.851
[13 empty] | SC | 0.535
[13 empty] | SD | 0.489
[13 empty] | TN | 0.7
[13 empty] | TX | 0.91
[13 empty] | UT | 1.591
[13 empty] | VT | 0.041
[13 empty] | VA | 0.633
[13 empty] | WA | 0.297
[13 empty] | WV | 1.93
[13 empty] | WI | 1.225
[13 empty] | WY | 2.054

## Peer Comparison
PEER COMPARISON
These two charts allow you to compare your current data center to 25 other data centers that were analyzed by LBNL.
Complete data were not available for all data centers - hence the gaps in the charts.
Answering questions 5 and 12 on the User Inputs A tab will populate the "Your Data Center" point in the IT Power Density chart.
Answering questions 5 and 6 on the User Inputs A tab will populate the "Your Data Center" point in the UPS Load Factor chart.

## UPS Efficiency
UPS EFFICIENCY
The "Typical UPS" data is drawn from the hidden UPS_data tab. It represents a typical double-conversion, 480-volt, modern (2014 to 2017), relatively efficient, UPS of 500 to 600 kW capacity.
The "Your UPS, Currently" point corresponds to the values in the Calculations table on the User Inputs tab.
Typical UPS
| Load Factor: | 10% | 20% | 30% | 40% | 50% | 60% | 70% | 80% | 90% | 100%
| Efficiency: | 89.83% | 94.23% | 95.62% | 96.11% | 96.33% | 96.44% | 96.5% | 96.49% | 96.47% | 96.47%

## Table AA (hidden)
SUPPORT FOR TABLE A |  | Color Key
Table AA provides content to support Table A on the User Inputs tab. |  | Content provided by the tool developer.
This tab is normally hidden. There is no user data entry on this tab.
Further description is provided at the bottom right of this tab.
Table AA: Basic Information
AA1 | AA2 | AA3 | AA4
Question Number | Question | Input Format | User's Input Value
Q1 | What is the annual average input power of the main IT transformer in kW? | [decimal number >= 0] | 650
Q2 | What is the annual average output power of the main IT transformer in kW? | [decimal number >= 0] | 620
Q3 | What is the nominal load capacity of the main IT transformer in kW? | [decimal number >= 0] | 850
Q4 | What is the annual average input power of the UPS system in kW? | [decimal number >= 0] | 580
Q5 | What is the annual average output power of the UPS system in kW? | [decimal number >= 0] | 500
Q6 | What is the total load capacity of all active UPS modules in kW? | [decimal number >= 0] | 750
Q7 | What is the UPS manufacturer's claimed efficiency at the calculated load factor shown at right? | [percentage >= 0%] | 0%
Q8 | What is the annual average total PDU input power in kW? | [decimal number >= 0] | 525
Q9 | What is the annual average total PDU output power in kW? | [decimal number >= 0] | 500
Q10 | What is the total load capacity of all active PDUs in kW? | [decimal number >= 0] | 600
Q11 | What is the annual average backup generator engine block heater power demand in kW? | [decimal number >= 0] | 10
Q12 | What is the data center floor area in sq. ft.? | [whole number >= 0] | 10000
Q13 | What is the annual average IT equipment power demand in kW? | [decimal number >= 0] | 515
Q14 | What is the annual average lighting power demand in kW for the data center? | [decimal number >= 0] | 20
Q15 | What is the annual average unit cost of electricity in ¢/kWh? | [decimal number >= 0] | 15
Table AA Description
Column
|  |  |  | AA1 | Question Number | Table AA supports questions number 1 through 15.
|  |  |  | AA2 | Question | The text for each question is entered here by the tool developer; the User Inputs tab reads and displays these cells.
|  |  |  | AA3 | Input Format | This column describes the type of numeric answer expected.
|  |  |  | AA4 | User's Input Value | This column simply repeats the input values from the User Inputs A tab, for trouble-shooting purposes.

## Table BB (hidden)
SUPPORT FOR TABLE B | [6 empty] | Color Key
Table BB provides content to support Table B on the Action Results tab, and performs savings calculations. | [6 empty] | Headings and separators.
This tab is normally hidden. There is no user data entry on this tab. | [6 empty] | Content provided by the tool developer.
Further description is provided at the bottom right of this tab. | [6 empty] | Space for future expansion, if needed.
Unused cells.
Table BB: Efficiency Information and Potential Actions
Questions, Input Options, User's Inputs |  |  |  |  | Potential Actions Based on User's Inputs | [5 empty] | Predicted Post-Implementation Performance |  |  |  | Lookup Tables: Estimated Percent Savings Due to Performance Improvement | [5 empty] | Estimated Savings and Simple Payback Calculations
BB1 | BB2 | BB3 | BB4 | BB5 | BB6 | BB7 | BB8 | BB9 | BB10 | BB11 | BB12 | BB13 | BB14 | BB15 | BB16 | BB17 | BB18 | BB19 | BB20 | BB21 | BB22 | BB23 | BB24 | BB25 | BB26 | BB27 | BB28
Question Number | Question | Input Options | User's Input Value | Calc. | Potential Actions | Input Options |  |  |  |  | Any Pursued Actions? | Question | Input Options | Value | Pre-Implementation Performance Level | Post-Implementation Performance Level |  |  |  | Savings Apply To | Pre-Implementation Performance Level | Post-Implementation Performance Level | Estimated Savings |  |  | Implementation Cost | Simple Payback
[6 empty] | Input Option(s) Resulting in Potential Actions |  |  | Input Option Resulting in No Action Required | Insufficient Information
[6 empty] | Option 1 | Option 2 | Option 3 | [14 empty] | % | kWh/yr | $/yr | $ | years
Q16 | What is the building power factor? | <0.9 | Do not know. |  |  | <0.9 |  |  | ≥0.9 | Do not know. | No | This tool assumes the new building power factor will be: |  | N/A |  | <0.9 | ≥0.9 |  |  | Total IT Power Chain Loss | Do not know. | N/A | 0 | 0 | 0 | 0 | 0
|  | ≥0.9 |  |  | Action 1 | Maintain Power Factor at Main Feeder Panel at 0.90 or Higher. |  |  |  | Investigate building power factor. |  |  |  |  | <0.9 | 0 | 2
|  | Do not know. | [12 empty] | ≥0.9 | 0 | 0
Q17 | What is the building total harmonic current distortion (THD) at main feeder panel? | >5% | Do not know. |  |  | >5% |  |  | ≤5% | Do not know. | No | This tool assumes the new building total harmonic current distortion (THD) at the main feeder panel will be: |  | N/A |  | >5% | ≤5% |  |  | Total IT Power Chain Loss | Do not know. | N/A | 0 | 0 | 0 | 0 | 0
|  | ≤5% |  |  | Action 1 | Maintain Total Harmonic Distortion at Main Feeder Panel at 5% or Less. |  |  |  | Investigate building total harmonic current distortion (THD) at main feeder panel. |  |  |  |  | >5% | 0 | 0.5
|  | Do not know. | [12 empty] | ≤5% | 0 | 0
Q18 | Are the loads balanced between all phases for the transformers, UPSs, and PDUs? | Out of balance by more than 10%. | Do not know. |  |  | Out of balance by more than 10%. |  |  | Balanced to within 10% or less. | Do not know. | No | This tool assumes the new loads on all phases for the transformers, UPSs, and PDUs will be: |  | N/A |  | Out of balance by more than 10%. | Balanced to within 10% or less. |  |  | Total IT Power Chain Loss | Do not know. | N/A | 0 | 0 | 0 | 0 | 0
|  | Balanced to within 10% or less. |  |  | Action 1 | Maintain Balanced Loads Between Phases. |  |  |  | Determine the load balance between phases for all transformers, UPSs, and PDUs. |  |  |  |  | Out of balance by more than 10%. | 0 | 0.5
|  | Do not know. | [12 empty] | Balanced to within 10% or less. | 0 | 0
Q19 | What is the age and type of the main transformer serving the IT power chain? | Temp rise ≥150 C and age >15 years old. | Do not know. |  |  | Temp rise ≥150 C and age >15 years old. | Temp rise ≥150 C and age ≤15 years old. | Temp rise < 150 C and age ≥ 15 years old. | Temp rise < 150 C and age < 15 years old. | Do not know. | No | This tool assumes the new age and type of the main transformer serving the IT power chain will be: |  | N/A |  | Temp rise ≥150 C and age >15 years old. | Temp rise ≥150 C and age ≤15 years old. | Temp rise < 150 C and age ≥ 15 years old. | Temp rise < 150 C and age < 15 years old. | Loss in Main Transformer Serving IT Power Chain | Do not know. | N/A | 0 | 0 | 0 | 0 | 0
|  | Temp rise ≥150 C and age ≤15 years old. |  |  | Action 1 | Use High Efficiency MV and LV Transformers. | Use High Efficiency MV and LV Transformers. | Use High Efficiency MV and LV Transformers. |  | Determine the age and type of the main transformer serving the IT power chain. |  |  |  |  | Temp rise ≥150 C and age >15 years old. | 0 | 0 | 0 | 1
|  | Temp rise < 150 C and age ≥ 15 years old. | [12 empty] | Temp rise ≥150 C and age ≤15 years old. | 0 | 0 | 0 | 1
|  | Temp rise < 150 C and age < 15 years old. | [12 empty] | Temp rise < 150 C and age ≥ 15 years old. | 0 | 0 | 0 | 1
|  | N/A (no main IT transformer). | [12 empty] | Temp rise < 150 C and age < 15 years old. | 0 | 0 | 0 | 0
Do not know.
Q20 | Is there an active UPS? | Yes. | Yes. | 86.21% |  | 90% |  |  | No. | Do not know. | Yes | What will the new UPS load factor be? | 10% | 80% | [5 empty] | UPS System Loss | 86.21% | 96.49% | 77.2645 | 541469.4994 | 81220.4249 | 300000 | 3.6937
|  | No. |  |  | Action 1 | Shut Down UPS Modules when Redundancy Level is High Enough. |  |  |  | Determine if you have any active UPS modules. |  |  | 20%
|  | Do not know. |  |  | Action 2 | Install a Modular UPS. | [6 empty] | 30%
[5 empty] | Action 3 | Right-Size the UPS. | [6 empty] | 40%
[5 empty] | Action 4 | Replace the UPS with a More Efficient Unit. | [6 empty] | 50%
60%
70%
80%
90%
100%
N/A
Q21 | Is the UPS operating in eco-mode? | Yes. | Do not know. |  |  | No. |  |  | Yes. | Do not know. | No | This tool assumes the UPS eco-mode feature will be activated. |  | N/A |  | Yes. | No. |  |  | UPS System Loss | Do not know. | N/A | 0 | 0 | 0 | 0 | 0
|  | No. |  |  | Action 1 | Implement a Switching UPS |  |  |  | Determine if the UPS has eco-mode capability. |  |  |  |  | Yes. | 0 | 0
|  | N/A (No UPS, or no eco-mode capability). | [12 empty] | No. | 3 | 0
Do not know.
Q22 | Are the UPS DC capacitors >5 years old? | Yes. | Do not know. |  |  | Yes. |  |  | No. | Do not know. | No | This tool assumes the UPS DC capacitors will be replaced with new ones. |  | N/A |  | Yes. | No. |  |  | UPS System Loss | Do not know. | N/A | 0 | 0 | 0 | 0 | 0
|  | No. |  |  | Action 1 | Change UPS DC Capacitors. |  |  |  | Determine if UPS DC capacitors are older than 5 years. |  |  |  |  | Yes. | 0 | 0.5
|  | Do not know. | [12 empty] | No. | 0 | 0
N/A (no UPS).
Q23 | What is the power source for non-critical loads? | UPS. | Do not know. |  |  | UPS. |  |  | Utility power. | Do not know. | No | This tool assumes that non-critical loads will no longer be served by the UPS. |  | N/A |  | UPS. | Utility power. |  |  | UPS System Loss | Do not know. | N/A | 0 | 0 | 0 | 0 | 0
|  | Utility power. |  |  | Action 1 | Ensure Non-Critical Loads are Not Connected to the UPS. |  |  |  | Investigate if non-critical loads are fed from the UPS. |  |  |  |  | UPS. | 0 | 1
|  | Do not know. | [12 empty] | Utility power. | 0 | 0
Q24 | What is the age and type of the transformers in the PDUs? | Temp rise ≥150 C and age >15 years old. | Do not know. |  |  | Temp rise ≥150 C and age >15 years old. | Temp rise ≥150 C and age ≤15 years old. | Temp rise < 150 C and age ≥ 15 years old. | Temp rise < 150 C and age < 15 years old. | Do not know. | No | This tool assumes the new age and type of the transformers in the PDUs will be: |  | N/A |  | Temp rise ≥150 C and age >15 years old. | Temp rise ≥150 C and age ≤15 years old. | Temp rise < 150 C and age ≥ 15 years old. | Temp rise < 150 C and age < 15 years old. | Total PDU Loss | Do not know. | N/A | 0 | 0 | 0 | 0 | 0
|  | Temp rise ≥150 C and age ≤15 years old. |  |  | Action 1 | Use High Efficiency MV and LV Transformers. | Use High Efficiency MV and LV Transformers. | Use High Efficiency MV and LV Transformers. |  | Determine the age and type of the transformers in the PDUs. |  |  |  |  | Temp rise ≥150 C and age >15 years old. | 0 | 0 | 0 | 1
|  | Temp rise < 150 C and age ≥ 15 years old. | [12 empty] | Temp rise ≥150 C and age ≤15 years old. | 0 | 0 | 0 | 1
|  | Temp rise < 150 C and age < 15 years old. | [12 empty] | Temp rise < 150 C and age ≥ 15 years old. | 0 | 0 | 0 | 1
|  | N/A (no transformers in PDUs). | [12 empty] | Temp rise < 150 C and age < 15 years old. | 0 | 0 | 0 | 0
Do not know.
Q25 | What is the average load factor for the active PDUs that contain transformers? | <25% | Do not know. |  |  | <25% | ≥25-50% |  | >50% | Do not know. | No | What will the average load factor for the active PDUs that contain transformers be? | <25% | >50% |  | <25% | ≥25-50% | >50% |  | Total PDU Loss | Do not know. | >50% | 0 | 0 | 0 | 0 | 0
|  | ≥25-50% |  |  | Action 1 | Consolidate Transformer Loads | Consolidate Transformer Loads |  |  | Determine the load factors for active PDUs that contain a transformer. |  |  | ≥25-50% |  | <25% | 0 | 1 | 5
|  | >50% | [10 empty] | >50% |  | ≥25-50% | 0 | 0 | 1
|  | Do not know. | [10 empty] | N/A |  | >50% | 0 | 0 | 0
Q26 | What is the IT equipment power factor? | <0.9 | Do not know. |  |  | <0.9 |  |  | ≥0.9 | Do not know. | No | This tool assumes the new power factor for the IT equipment will be: |  | N/A |  | <0.9 | ≥0.9 |  |  | Total IT Equipment Energy Use | Do not know. | N/A | 0 | 0 | 0 | 0 | 0
|  | ≥0.9 |  |  | Action 1 | Retrofit IT Equipment to Maintain High Power Factor and Low Total Harmonic Distortion. |  |  |  | Measure the IT equipment power factor. |  |  |  |  | <0.9 | 0 | 2
|  | Do not know. | [12 empty] | ≥0.9 | 0 | 0
Q27 | What is the power source for the IT racks? | Alternating current (AC). | Do not know. |  |  | Alternating current (AC). |  |  | Direct current (DC). | Do not know. | No | This tool assumes the new power source for the IT racks will be: |  | N/A |  | Alternating current (AC). | Direct current (DC). |  |  | UPS System Loss | Do not know. | N/A | 0 | 0 | 0 | 0 | 0
|  | Direct current (DC). |  |  | Action 1 | Supply DC Voltage to IT Rack. |  |  |  | Investigate if IT racks are fed from an AC or DC power source. |  |  |  |  | Alternating current (AC). | 0 | 40
|  | Do not know. | [12 empty] | Direct current (DC). | 0 | 0
Q28 | What is the power source for the emergency generator block heater(s)? | Utility power. | Do not know. |  |  | Utility power. |  |  | Alternate power source, e.g. solar. | Do not know. | No | This tool assumes the new power source for the emergency generator block heater(s) will be: |  | N/A |  | Utility power. | Alternate power source, e.g. solar. |  |  | Backup Generator Engine Block Heater Total Energy Use | Do not know. | N/A | 0 | 0 | 0 | 0 | 0
|  | Alternate power source, e.g. solar. |  |  | Action 1 | Use Alternate Power Source to Warm Generator Blocks. |  |  |  | Investigate power source for generator block heater(s). |  |  |  |  | Utility power. | 0 | 0.5
|  | Do not know. | [12 empty] | Alternate power source, e.g. solar. | 0 | 0
Q29 | Does the block heater(s)/heater water jacket for emergency generator(s) operate with thermostat control? | No. | Do not know. |  |  | No. |  |  | Yes. | Do not know. | No | This tool assumes the block heater(s)/heater water jacket for emergency generator(s) will be equipped with with thermostat control. |  | N/A |  | No. | Yes. |  |  | Backup Generator Engine Block Heater Total Energy Use | Do not know. | N/A | 0 | 0 | 0 | 0 | 0
|  | Yes. |  |  | Action 1 | Apply Thermostat Control to Generator Block Heaters. |  |  |  | Investigate if block heater(s) operate with thermostat control. |  |  |  |  | No. | 0 | 0.5
|  | Do not know. | [12 empty] | Yes. | 0 | 0
Q30 | Is the data center lighting well-designed? | No, the data center is over-lit and/or light is provided where it is not needed. | Do not know. |  |  | No, the data center is over-lit and/or light is provided where it is not needed. |  |  | Yes, sufficient light is provided only to the areas that need it. | Do not know. | No | This tool assumes the data center lighting will be reconfigured to provide light only to the areas that need it. |  | N/A |  | No, the data center is over-lit and/or light is provided where it is not needed. | Yes, sufficient light is provided only to the areas that need it. |  |  | Data Center Total Lighting Energy Use | Do not know. | N/A | 0 | 0 | 0 | 0 | 0
|  | Yes, sufficient light is provided only to the areas that need it. |  |  | Action 1 | Illuminate Work Areas Only. |  |  |  | Investigate the effectiveness of data center lighting. |  |  |  |  | No, the data center is over-lit and/or light is provided where it is not needed. | 0 | 15
|  | Do not know. |  |  | Action 2 | Coordinate Light Fixture Placement with IT Equipment Placement. | [8 empty] | Yes, sufficient light is provided only to the areas that need it. | 0 | 0
Q31 | How are the lights controlled in the data center? | No control (always on). | No control (always on). |  |  | No control (always on). | Timeclock. | Manual Control. | Occupancy Sensor. | Do not know. | Yes | The lights will be controlled in the data center by: | No control (always on). | Occupancy Sensor. |  | No control (always on). | Timeclock. | Manual Control. | Occupancy Sensor. | Data Center Total Lighting Energy Use | No control (always on). | Occupancy Sensor. | 70 | 122640 | 18396 | 15000 | 0.81539
|  | Timeclock. |  |  | Action 1 | Control Lighting with a Timeclock. | Implement Manually Controlled Zone Lighting Control. | Install Occupancy Sensors to Control Lights. |  | Investigate how the data center lighting is controlled. |  |  | Timeclock. |  | No control (always on). | 0 | 25 | 50 | 70
|  | Manual Control. |  |  | Action 2 | Implement Manually Controlled Zone Lighting Control. | Install Occupancy Sensors to Control Lights. | [5 empty] | Manual Control. |  | Timeclock. | 0 | 0 | 25 | 35
|  | Occupancy Sensor. |  |  | Action 3 | Install Occupancy Sensors to Control Lights. | [6 empty] | Occupancy Sensor. |  | Manual Control. | 0 | 0 | 0 | 25
|  | Do not know. | [10 empty] | N/A |  | Occupancy Sensor. | 0 | 0 | 0 | 0
Q32 | What type of lamps are installed in the data center? | Compact Fluorescent (CFL) or T12 Fluorescent. | Do not know. |  |  | Compact Fluorescent (CFL) or T12 Fluorescent. | T8 Fluorescent. | T5 Fluorescent. | LED. | Do not know. | No | The new type of lamps to be installed in the data center are: | Compact Fluorescent (CFL) or T12 Fluorescent. |  |  | Compact Fluorescent (CFL) or T12 Fluorescent. | T8 Fluorescent. | T5 Fluorescent. | LED. | Data Center Total Lighting Energy Use | Do not know. |  | 0 | 0 | 0 | 0 | 0
|  | T8 Fluorescent. |  |  | Action 1 | Install Linear Fluorescent T8 Fixtures. | Install Linear Fluorescent T5 Fixtures. | Install LED Fixtures. |  | Investigate the type of lighting installed in th data center. |  |  | T8 Fluorescent. |  | Compact Fluorescent (CFL) or T12 Fluorescent. | 0 | 15 | 25 | 35
|  | T5 Fluorescent. |  |  | Action 2 | Install Linear Fluorescent T5 Fixtures. | Install LED Fixtures. | [5 empty] | T5 Fluorescent. |  | T8 Fluorescent. | 0 | 0 | 10 | 20
|  | LED. |  |  | Action 3 | Install LED Fixtures. | [6 empty] | LED. |  | T5 Fluorescent. | 0 | 0 | 0 | 10
|  | Do not know. | [10 empty] | N/A |  | LED. | 0 | 0 | 0 | 0
Table BB Description
Questions, Input Options, User's Inputs
Column
[28 empty] | BB1 | Question Number |  |  | Table BB supports questions number 22 through 39.
[28 empty] | BB2 | Question |  |  | The text for each question is entered here by the tool developer; the User Inputs tab reads and displays these cells.
[28 empty] | BB3 | Input Options |  |  | This column supplies the options for the pull-down lists on the User Inputs tab.
[28 empty] | BB4 | User's Input Value |  |  | This column simply repeats the input values from the User Inputs tab, for trouble-shooting purposes.
[28 empty] | BB5 | Calc. |  |  | Questions 27 and 28 involve an intermediate calculation, performed on the User Inputs tab. This column simply repeats these values from the User Inputs tab, for trouble-shooting purposes.
Potential Actions Based on User's Inputs
Column
[28 empty] | BB6 | Potential Actions |  |  | This column shows how many potential actions this tool can suggest in response to the user's input for each question. Most questions currently have only one potential action; some have more.
[28 empty] | BB7 | Input Options | Input Option(s) Resulting in Potential Actions | Option 1 | These three columns show the actions that will be presented in response to the user's input. If the user inputs the option shown under the Option 1 heading, the actions listed under Option 1 will be presented. Likewise for Option 2 and Option 3.
[28 empty] | BB8 |  |  | Option 2
[28 empty] | BB9 |  |  | Option 3
[28 empty] | BB10 |  | Input Option(s) Resulting in No Action Required |  | If the user inputs the option shown under this heading, no actions are presented.
[28 empty] | BB11 |  | Insufficient Information |  | If the user inputs "Do not know", the text listed below this heading provides a suggestion on how to obtain the requested information.
Predicted Post-Implementation Performance
[28 empty] | BB12 | Any Pursued Actions? |  |  | On the Action Results tab, if the user indicated that they will pursue any of the presented actions, then the value in this column is "Yes", otherwise "No".
[28 empty] | BB13 | Question |  |  | This column supplies the text for the questions/assumptions that populate column C4 on the Action Results tab.
[28 empty] | BB14 | Input Options |  |  | This column supplies the options for the pull-down lists in column C5 on the Action Results tab, for the questions that have more than one post-implementation option.
[28 empty] | BB15 | Value |  |  | If there are no pursued actions, this column is set to "N/A". Otherwise, it: a) Contains the assumed post-implementation performance, or b) Repeats the input values from column C5 on the Action Results tab.
Lookup Tables: Estimated Percent Savings Due to Performance Improvement
Column
[28 empty] | BB16 | Pre-Implementation Performance Level |  |  | With the exception of Question 28, columns BB16 through BB21 contain lookup tables. Column BB16 repeats the input options from column BB3.
[28 empty] | BB17 | Post-Implementation Performance Level |  |  | The top of each lookup table repeats the input options from column BB3. The body of each lookup table is populated with percent savings values provided by the tool developer. These are estimates based on engineering experience. These lookup tables are referred to by the formulas in column BB24.
BB18
BB19
BB20
[28 empty] | BB21 | Savings Apply To |  |  | The estimated savings percentages apply to different areas of the power distribution chain.
Estimated Savings and Simple Payback Calculations
Column
[28 empty] | BB22 | Pre-Implementation Performance Level |  |  | Column BB22 repeats the user-selected option from column BB4. Exception: For question 27, the calculated UPS load factor in column BB5 is converted to one of the three options listed in column BB3.
[28 empty] | BB23 | Post-Implementation Performance Level |  |  | Column BB23 repeats the user-selected option from column BB15. Exception: For Question 28, the predicted post-implementation UPS load factor shown in column BB15 is used to look up the predicted post-implementation UPS efficiency value from the UPS Efficiency tab.
[28 empty] | BB24 | Estimated Savings |  | % | If columns BB22 and BB23 contain valid options, the estimated percent savings is drawn from the corresponding lookup table in columns BB16 through BB20. Exception: For question 28, the percent savings is calculated as column BB23 minus column BB22.
[28 empty] | BB25 |  |  | kWh/yr | Questions 22 through 36: The annual energy savings are calculated as the percent value in column BB24 times the annual energy loss in the IT branch of the power chain. The latter value is calculated on the User Inputs tab, below Table A. Exception: For question 28, the annual energy savings are calculated as (1/BB22 - 1/BB23) * Q3 * 8760 hrs/yr. Questions 37 through 39: The annual energy savings are calculated as the percent value in column BB24 times the annual energy use of the lighting system. The latter value is provided by the user in response to question 7 on the User Inputs tab.
[28 empty] | BB26 |  |  | $/yr | The annual energy cost savings is simply the energy savings from column BB25 times the annual average unit cost of electricity (question 8 on the User Inputs tab).
[28 empty] | BB27 | Implementation Cost |  | $ | This column simply repeats the input values from column C9 on the Action Results tab.
[28 empty] | BB28 | Simple Payback |  | years | This is calculated as the implemention cost (column BB27), divided by the energy cost savings (column BB26).

## Table DD (hidden)
ESTIMATED SAVINGS CALCULATIONS
This tab calculates the values that populate Table D on the Savings Summary tab.
This tab is normally hidden. There is no user data entry on this tab.
Cap the total UPS System Loss savings at: |  |  |  | 80 | % | This value is from the Savings Summary tab.
Cap the total Data Center Lighting savings at: |  |  |  | 80 | % | This value is from the Savings Summary tab.
Table DD: Estimated Savings
DD1 | DD2 | DD3 | DD4 | DD5 | DD6 | DD7 | DD8 | DD9 | DD10 | DD11 | DD12 | DD13
For Actions That Affect: |  |  |  | Percent Savings Raw Sum | Percent Savings Capped At | Annual Energy Use, Pre-Implementation | Percent Savings | Annual Energy Savings | Annual Energy Use, Post-Implementation | Annual Energy Cost Savings | Implementation Cost | Simple Payback
|  |  |  | % | % | kWh/yr | % | kWh/yr | kWh/yr | $/yr | $ | years
IT Systems | IT Power Chain | Power Transformation Equipment | Main IT Transformer | 0 |  | 262800 | 0 | 0 | 262800 | 0 | 0 | N/A
|  |  | UPS System | 77.2645 | 77.2645 | 700800 | 77.2645 | 541469.4994 | 159330.5006 | 81220.4249 | 300000 | 3.6937
|  |  | All PDUs Combined | 0 |  | 219000 | 0 | 0 | 219000 | 0 | 0 | N/A
|  |  | Entire IT Power Chain | 0 |  | 1182600 | 0 | 0 | 1182600 | 0 | 0 | N/A
|  |  | Total IT Power Chain Loss |  |  | 1182600 | 45.7864 | 541469.4994 | 641130.5006 | 81220.4249 | 300000 | 3.6937
|  | IT Equipment |  | 0 |  | 4511400 | 0 | 0 | 4511400 | 0 | 0 | N/A
|  | Total IT Power Chain |  |  |  | 5694000 | 9.5095 | 541469.4994 | 5152530.5006 | 81220.4249 | 300000 | 3.6937
| Backup Generator Engine Block Heaters |  |  | 0 |  | 87600 | 0 | 0 | 87600 | 0 | 0 | N/A
| Total IT Systems |  |  |  |  | 5781600 | 9.3654 | 541469.4994 | 5240130.5006 | 81220.4249 | 300000 | 3.6937
Data Center Lighting System |  |  |  | 70 | 70 | 175200 | 70 | 122640 | 52560 | 18396 | 15000 | 0.81539
Totals | [5 empty] | 5956800 | 11.1488 | 664109.4994 | 5292690.5006 | 99616.4249 | 315000 | 3.1621
Table DD Description
Column
[13 empty] | DD1 - DD4 | For Actions That Affect: |  | This tool applies percent savings estimates to the different elements of the electric system. To see which actions affect which element, refer to the Action Results tab, column C7 in Table C.
[13 empty] | DD5 | Percent Savings Raw Sum | % | This column accumulates the percent savings from all pursued actions, that apply to the given element of the power chain. This tool does not account for interactive effects between actions, so if multiple actions are selected it is possible to obtain unreasonable savings percentages. This issue is addressed by column DD6.
[13 empty] | DD6 | Percent Savings Capped At | % | If necessary, the savings for the UPS System and the lighting system are capped at the percent values entered by the user on the Savings Summary tab.
[13 empty] | DD7 | Annual Energy Use, Pre-Implementation | kWh/yr | These values are copied from the Calculations table on the User Inputs A tab.
[13 empty] | DD8 | Percent Savings | % | Minimum of the values in columns DD5 and DD6. For the Totals rows, the percent savings is caluclated as the Annual Energy Savings (column DD9) divided by the Annual Energy Use, Pre-Implementation (column DD7).
[13 empty] | DD9 | Annual Energy Savings | kWh/yr | Calculated as Percent Savings (column DD8) times the Annual Energy Use, Pre-Implementation (column DD7). For the Totals rows, the savings are the sum of the preceding rows.
[13 empty] | DD10 | Annual Energy Use, Post-Implementation | kWh/yr | Equal to the Annual Energy Use, Pre-Implementation (column DD7) minus the Annual Energy Savings (column DD9).
[13 empty] | DD11 | Annual Energy Cost Savings | $/yr | Equal to the value in column DD10 times the annual average electric cost rate entered on the User Inputs A tab, Table A, Question 15.
[13 empty] | DD12 | Implementation Cost | $ | Accumulates the implementation costs from the Action Results tab, for all the pursued actions that affect the given element of the electric system.
[13 empty] | DD13 | Simple Payback | years | Calculated as column DD12 divided by column DD11.

## DC_BM_data (hidden)
DATA CENTER BENCHMARKS
This tab is normally hidden. There is no user data entry on this tab.
Data from columns E11 and E19 are used to populate the charts on the Peer Comparison tab.
The bottom two rows of Table E include calculations based on the user's input data to this tool.
Table E: Data Center Benchmarks
E1 | E2 | E3 | E4 | E5 | E6 | E7 | E8 | E9 | E10 | E11 | E12 | E13 | E14 | E15 | E16 | E17 | E18 | E19 | E20 | E21 | E22 | E23
Bench-mark Number | UPS Load Capacity |  |  |  |  | UPS System Efficiency |  |  |  | UPS Load Factor |  |  |  | DC Floor Area |  |  |  | IT Avg Power Density (Actual) |  |  |  | Additional Notes (load factor, avg power drawn, # UPS, UPS power and hours)
| UPS Rating |  | Notes |  |  | Measured UPS Output kW / Measured UPS Input kW | Notes |  |  | IT Power / UPS Load Capacity | Notes |  |  | Floor Area | Notes |  |  | IT Avg Power (actual) / DC Floor Area If IT avg is NA then use total IT power | Notes
| kVA | kW | Note | Date | By | % | Note | Date | By |  | Note | Date | By | ksf | Note | Date | By | W/sf | Note | Date | By
1 | NA | NA |  |  |  | 0 |  |  |  | 0 |  |  |  | 62.87 |  |  |  | 23.86 |  |  |  | load factor: 0.96, avg 3540kVA, 2,990 kW, Liebert UPS 480V constant delivery voltage, 4 Cummins diesel generator with 2,000 kW each for 40 hours
2 | NA | NA |  |  |  | 0 |  |  |  | 0 |  |  |  | 60.4 |  |  |  | 33.77 |  |  |  | load factor: 0.96, avg. 4190kVA, 4000 kW, 5 generators providing 1500W each for 40 hours
3 | NA | NA |  |  |  | 0 |  |  |  | 0 |  |  |  | 25 |  |  |  | 41.6 |  |  |  | load factor: 0.97, avg. 1780kVA, 1760 kW, 3 generators providing 1500W each for 8 hours
4 | NA | NA |  |  |  | 78.5 | 92%(rated), 78.5%(measured) | 2010-01-25 | SRG | 0 |  |  |  | 8.9 |  |  |  | 4.12 |  |  |  | 450 kW Emerson Accupower UPS (shared with DC 5), battery supplies power for 30 mins
5 | NA | NA |  |  |  | 78.5 | 92%(rated), 78.5%(measured) | 2010-01-25 | SRG | 0 |  |  |  | 8.56 |  |  |  | 4.98 | 7% of DC is occupied, with 100% occupancy the total IT load=590kW, area=8.56ksft; computer load density=68kw/sf | 2010-01-25 | unknown | 450 kW Emerson Accupower UPS (shared with DC 4), battery supplies power for 30 mins
6 | 225 | 180 |  |  |  | 0 |  |  |  | 0 |  |  |  | 16 |  |  |  | 35.31 |  |  |  | UPS has 225 kVA capacity and is 10% loaded
7 | 225 | 180 |  |  |  | 94 |  |  |  | 0 |  |  |  | 2.4 |  |  |  | 64.54 |  |  |  | 400 kW diesel generator for 10 hrs.
8 | 210 | 168 | UPS1: 160 kVA UPS2: 50 kVA | 2010-01-25 | SRG | 91.5 |  |  |  | 0 |  |  |  | 2.5 |  |  |  | 47.64 |  |  |  | International Power Machine 160 kVA, Chloride 50 Power Electronics 50 kVA UPS, 750 kW diesel generator for 10 hours
9 | 4725 | 3780 | UPS1: 2225 kVA UPS2: 2500 kVA | 2010-01-25 | SRG | 80 |  |  |  | 0.4 |  |  |  | 74 |  |  |  | 19.19 |  |  |  | UPS1:Exide UPS2:Teledyne 4 3MW generators (diesel) for 8 days
10 | 375 | 300 | Output - UPS1,2,3: 30kW UPS4: 40kW UPS5,6: 44.6kW | 2010-01-25 | SRG | 80 |  |  |  | 0 |  |  |  | 26.2 |  |  |  | 8.47 |  |  |  | 6 375kVA Liebert UPS, 3 750kW diesel generators backup,
11 | 5550 | 4440 | 5x 1100 kVA UPS | 2010-01-25 | SRG | 81.4 | UPS1:68% UPS2:87% UPS3:81% UPS4: 86% UPS5: 85% | 2010-01-25 | SRG | 0.34 |  |  |  | 73 |  |  |  | 14.51 |  |  |  | 5 1100kVA Liebert UPS, 2 2000 kW diesel generators
12 | 1000 | 800 | 2x 500 kVA Liebert UPS | 2010-01-25 | SRG | 83.9 | UPS1:89.6 UPS2:47.3 combined:83.9 | 2010-01-25 | SRG | 0 |  |  |  | 8.15 |  |  |  | 23.31 |  |  |  | 2 substations, N+1 redundancy, UPS (100 mins), no generator, PDU efficiency 94.8%
13 | 4500 | 3600 | UPS1: 1500 kVA UPS2: 3000 kVA | 2010-01-25 | SRG | 0 |  |  |  | 0.42 |  |  |  | 119 | Ref. Tschudi report | 2010-01-25 | SRG | 29 |  |  |  | 2 on-site substations:10.5MVA, 3 7.5MW gas-turbine generators,
14 | 4500 | 3600 | UPS1: 1500 kVA UPS2: 3000 kVA | 2010-01-25 | SRG | 0 |  |  |  | 0.42 |  |  |  | 83.47 |  |  |  | 29.16 |  |  |  | 2800kW feed, 10 1400kW diesel generators, 6 UPS systems of 15000 & 3000kVA,
15 | NA | NA |  |  |  | 93 | Loss of UPS: 7% | 2010-01-25 | SRG | 0 |  |  |  | 27.501 |  |  |  | 15.71
16 | 5680 | 4544 |  |  |  | 0 |  |  |  | 0.33 |  |  |  | 10 |  |  |  | 37.7 |  |  |  | 2 HITEC generators, 8 HITEC generators as UPS
17 | 5680 | 4544 |  |  |  | 0 |  |  |  | 0.33 |  |  |  | 10 |  |  |  | 16.5 |  |  |  | 2 HITEC generators, 8 HITEC generators as UPS
18 | 2250 | 1800 |  |  |  | 0 |  |  |  | 0.83 |  |  |  | 7.425 |  |  |  | 19.93 |  |  |  | supply: 3 5000A at 480V buses each with 3 750kVA UPS
19 | 2250 | 1800 |  |  |  | 0 |  |  |  | 0.83 |  |  |  | 7.425 |  |  |  | 56.03 |  |  |  | supply: 3 5000A at 480V buses each with 3 750kVA UPS
20 | NA | NA |  |  |  | 0 |  |  |  | 0 |  |  |  | 3.024 |  |  |  | 61.18 |  |  |  | non-critical facility, no UPS, no generator, no humidifiers, no electrical reliability component
21 | NA | NA |  |  |  | 0 |  |  |  | 0 |  |  |  | 8.58 |  |  |  | 62.94 |  |  |  | non-critical facility, no UPS, no generator, no humidifiers, no electrical reliability component, no PDU
22 | 2000 | 1600 |  |  |  | 0 |  |  |  | 0.94 |  |  |  | 10 |  |  |  | 56.5 |  |  |  | 2 standby generators each rated at 1500kW/kVA
23 | NA | NA |  |  |  | 0 |  |  |  | 0 |  |  |  | 12.26 |  |  |  | 89
24 | NA | NA |  |  |  | 91 |  |  |  | 0 |  |  |  | 3.23 |  |  |  | 137 | from summary | 2010-01-25 | SRG
25 | 3000 | 2400 | 2400kW=3000kVA power factor=0.8 kW/PF=kVA | 2010-01-25 | SRG | 86 | load factor = 20% | 2010-01-25 | unknown | 0.63 |  |  |  | 0 | DC area missing | 2010-01-25 | SRG | 0 | DC area missing | 2010-01-25 | SRG
Your Data Center |  | 750 | kVA: Workbook currently does not ask for kVA. kW: From Question 6 (asks for ACTIVE capacity). | 2020-09-09 | KT | 86.2069 | From the Calculations section of the User Inputs A tab. | 2020-09-09 | KT | 0.66667 | From the Calculations section of the User Inputs A tab. | 2020-09-09 | KT | 10 | From Question 12. | 2020-09-09 | KT | 50 | From Questions 5 and 12. | 2020-09-09 | KT
Your Data Center, After |  |  | Workbook currently does not ask for post-implementation UPS capacity. | 2020-02-24 | KT | 96.49 | From Question 20, post-implementation. | 2020-09-09 | KT | 0.8 | From Question 20, post-implementation. | 2020-09-09 | KT | 10 | Tool assumes floor area does not change. | 2020-02-24 | KT | 50 | Tool assumes IT equipment load does not change. | 2020-02-24 | KT

## UPS_data (hidden)
UPS DATA
This tab is normally hidden. There is no user data entry on this tab.
This tab presents data for a sampling of modern, double-conversion, relatively efficient UPSs.
All UPSs shown here are 480-volt models, of 500 kW or 600 kW capacity.
If any UPS here has "eco-mode" capability, the efficiency data presented here represents the UPS NOT operating in eco-mode.
The source documents provide numeric efficiency values only at four load factors: 25%, 50%, 75%, 100% (green shaded cells below).
Some source documents provide a graphic efficiency curve. In these cases, the efficiency values in the non-shaded cells were estimated by examining the graphs.
The remaining efficiency values in the non-shaded cells were estimated by ensuring a smooth curve in the chart shown below.
The average values at the bottom of the table are intended to represent a typical, modern, efficient double-conversion UPS.
Table F: UPS Efficiency Data
F1 | F2 | F3 | F4 | F5 | F6 | F7 | F8 | F9 | F10 | F11 | F12 | F13 | F14 | F15 | F16 | F18 | F17
Model | Year | Capacity | Load Factor | [12 empty] | Range of UPS Capacities Available in Model Line | Source of Technical Specifications
|  |  | 0% | 10% | 20% | 25% | 30% | 40% | 50% | 60% | 70% | 75% | 80% | 90% | 100%
Galaxy VX | 2017 | 500 kW | 0% | 90% | 95% | 95.8% | 96.05% | 96.3% | 96.4% | 96.35% | 96.25% | 96.2% | 96.15% | 96.1% | 96.1% | 500 - 1500 kW | https://download.schneider-electric.com/files?&p_enDocType=Specification%20guide&p_File_Name=MBPN-A7TE49_R5_EN.pdf&p_Doc_Ref=SPD_MBPN-A7TE49_EN
Symmetra PX | 2016 | 500 kW | 0% | 92.5% | 95% | 95.5% | 95.8% | 96.1% | 96.3% | 96.37% | 96.41% | 96.4% | 96.37% | 96.32% | 96.3% | 250 - 500 kW | https://download.schneider-electric.com/files?&p_enDocType=Specification%20guide&p_File_Name=MBPN-9QECL6_R4_EN.pdf&p_Doc_Ref=SPD_MBPN-9QECL6_EN
Symmetra MW | 2014 | 600 kW | 0% | 87% | 92.7% | 94.1% | 95% | 95.94% | 96.3% | 96.59% | 96.83% | 96.9% | 96.95% | 97% | 97% | 400 - 1600 kW | https://download.schneider-electric.com/files?&p_enDocType=Specification%20guide&p_File_Name=MBPN-9N5KL3_R0_EN.pdf&p_Doc_Ref=SPD_MBPN-9N5KL3_EN
|  | AVERAGE | 0% | 89.83% | 94.23% | 95.13% | 95.62% | 96.11% | 96.33% | 96.44% | 96.5% | 96.5% | 96.49% | 96.47% | 96.47%

## Developer (hidden)
Developer Notes
This tab holds formatting and coding notes for this workbook.
This tab is normally hidden. There is no user data entry on this tab.
Excel version: | Excel 2007 & later (xlsx).
Color pallette/theme: | Excel 2010
Fonts and Colors
| Font | Color |  |  |  | Sample | Source | Use | Comments
|  | Generic Name | R | G | B
Headings | Franklin Gothic Medium | Dark Green | 1 | 122 | 62 | Heading | FEMP report template for Word. | Headings.
Body Text | Arial Narrow | Default (black) |  |  |  | Body text
Fills |  | Dark Green | 3 | 118 | 48 |  | FEMP report template for Word, front cover. |  | Not used in this workbook yet.
|  | Medium Green | 79 | 172 | 155 |  | FEMP report template for Word, front cover.
|  | Light Green | 146 | 208 | 80 |  | Selected for this workbook.
|  | Lightest Green | 201 | 231 | 167 |  | Selected for this workbook. | User input fields.
|  | Table Blue | 229 | 239 | 235 |  | FEMP report template for Word. | Table rows (first, third, fifth, etc). | Not used in this workbook yet.
|  | Light Blue | 204 | 255 | 255 |  | Selected for this workbook. | Content provided by developer.
|  | Medium Gray | 166 | 166 | 166 |  | Selected for this workbook. | Unused cells.
|  | Light Gray | 217 | 217 | 217 |  | Selected for this workbook. | Unused cells.
Tabs
Overview
User Inputs
Action Results
Savings Summary
Peer Comparison
UPS Efficiency
Table AA
Table BB
Table DD
DC_BM_data
Developer