## Data Center Energy Savings Calc
Calculating Energy Savings Using High Efficiency Power Conversion (UPS, AC-DC & DC-DC Power Supply ) in Server and other IT Applications; Rev 3.0 4/2005
Calculations Based on Typical Power Budget for a Dual 2.4 GHz Xeon Processor based 1U Server Rack
User Options | [6 empty] | Data Center Energy Savings Estimate
Adjust the options in the blue fields below to modify your energy savings scenario. |  |  |  |  | Reduction in Power Loss (Watt) | Reduction in Air Conditioning Power (Watt) | Total Savings (Watt) | Annual Energy Savings (MWh) | Annual Energy Savings ($) | NPV of Savings ($)
|  |  |  | UPS | 11546.5836 | 3939.6943 | 15486.2779 | 135.6598 | 13565.9795 | 47007.5516
| Data Center Options |  |  | AC/DC PS | 0 | 0 | 0 | 0 | 0 | 0
Number of racks in data center | 10 |  |  | DC/DC VRM | 0 | 0 | 0 | 0 | 0 | 0
Number of 1U Servers Per Rack | 40 |  |  |  |  | Total Data Center Savings | 15486.2779 | 135.6598 | 13565.9795 | 47007.5516
Electricity Cost | 0.1 | $/kWh |  |  |  | Total Savings per Rack | 1548.6278 | 13.566 | 1356.5979 | 4700.7552
Life Time | 4 | years |  | Savings/Server |  |  | 38.7157 | 0.33915 | 33.9149 | 117.5189
Discount Rate | 6% | percent
Overall Cooling System Efficiency | 1200 | Watt/Ton (12000 BTU)
VRM Options
Evaluate VRM efficiency? | 1
Power Supply Options
Evaluate PS efficiency? | 1
PS Nameplate Rating | 400 | watts
# of PS AC inputs (typical case) | 1
# PS AC inputs (high efficiency case) | 1
UPS Options
Preferred high efficiency UPS | 4
UPS nameplate rating (active power) | 250 | kW
Redundancy configuration of base case UPS | 2
Redundancy configuration of high efficiency UPS | 2
# of loaded UPSs: base case | 1
# of loaded UPSs: high efficiency case | 1
Power Budget: Improved VRM, Power Supply, UPS | [6 empty] | Percent Loads
|  | Typical Case |  | High Efficiency Case |  |  | Typical Case |  | High Efficiency Case
|  | Typical | Max | Typical | Max | Reduction in Power Loss | Typical | Max | Typical | Max
VRM Output Power (W) |  | 60 | 130 | 60 | 130
VRM Input Power (W) |  | 71.4286 | 154.7619 | 71.4286 | 154.7619 | 0
Total DC Power (W) |  | 131.4286 | 374.7619 | 131.4286 | 374.7619
PS Input AC Power (W) |  | 182.8045 | 505.3731 | 182.8045 | 505.3731 | 0 | 32.86% | 93.69% | 32.86% | 93.69%
Rack AC Input (kW) |  | 7.3122 | 20.2149 | 7.3122 | 20.2149 | 0
Total Protected Power (kW) |  | 73.1218 | 202.1493 | 73.1218 | 202.1493 | 0
UPS Input Power (kW) |  | 90.2738 | 235.0573 | 78.7272 | 206.7956 | 11.5466 | 29.25% | 80.86% | 29.25% | 80.86%
[6 empty] | 11.5466 | kW facility-wide
Power Budget: Improved UPS
|  | Typical Case |  | High Efficiency Case
|  | Min | Max | Min | Max | Reduction in Power Loss
VRM Output Power (W) |  | 60 | 130 | - | -
VRM Input Power (W) |  | 71.4286 | 154.7619 | - | -
Total DC Power (W) |  | 131.4286 | 374.7619 | - | -
PS Input AC Power (W) |  | 182.8045 | 505.3731 | - | -
Rack AC Input (kW) |  | 7.3122 | 20.2149 | - | -
Total Protected Power (kW) |  | 73.1218 | 202.1493 | 73.1218 | 202.1493
UPS Input Power (kW) |  | 90.2738 | 235.0573 | 78.7272 | 206.7956 | 11.5466
[6 empty] | 11.5466 | kW facility-wide
Power Budget: Improved Power Supply
|  | Typical Case |  | High Efficiency Case
|  | Min | Max | Min | Max | Reduction in Power Loss
VRM Output Power (W) |  | 60 | 130 | - | -
VRM Input Power (W) |  | 71.4286 | 154.7619 | - | -
Total DC Power (W) |  | 131.4286 | 374.7619 | 131.4286 | 374.7619
PS Input AC Power (W) |  | 182.8045 | 505.3731 | 182.8045 | 505.3731 | 0
Rack AC Input (kW) |  | 7.3122 | 20.2149 |  |  | 0
Total Protected Power (kW) |  | 73.1218 | 202.1493 |  |  | 0
UPS Input Power (kW) |  | 90.2738 | 235.0573
[6 empty] | 0 | kW facility-wide
Power Budget: Improved Power Supply and UPS
|  | Typical Case |  | High Efficiency Case
|  | Min | Max | Min | Max | Reduction in Power Loss
VRM Output Power (W) |  | 60 | 130 | - | -
VRM Input Power (W) |  | 71.4286 | 154.7619 | - | -
Total DC Power (W) |  | 131.4286 | 374.7619 | 131.4286 | 374.7619
PS Input AC Power (W) |  | 182.8045 | 505.3731 | 182.8045 | 505.3731 | 0
Rack AC Input (kW) |  | 7.3122 | 20.2149 | 7.3122 | 20.2149 | 0
Total Protected Power (kW) |  | 73.1218 | 202.1493 | 73.1218 | 202.1493 | 0
UPS Input Power (kW) |  | 90.2738 | 235.0573 | 78.7272 | 206.7956 | 11.5466
[6 empty] | 11.5466 | kW facility-wide
Note on A1: Work Funded by CEC PIER Program on Data Center Efficiency Administered by LBNL
Note on A38: # of UPSs that are loaded during normal operation, when there isn't an irregularity in utility power. We assume that these UPSs share the total load equally.
Note on A27: Peter Ostendorp: This number is changed by switching to a 2N or 2(N+1) power infrastructure in the UPS redundancy configuration.
Note on A12: Used to determine net present value of savings.
Note: analysis only takes energy costs and savings into account. HVAC energy savings and other secondary effects are currently ignored.

## Power Conversion Flowchart
120V AC
120V AC
Floppy Drive 0.5A CDROM Drive 0.8A Hard Drives, IDE, 4X 2.4A Blowers, 4X 6.6A
Mother Board 8.0A PCI Card 5A Hard Drives, IDE, 4X 1.2A Blowers, 4X 6.6A Keyboard & Mouse 0.5A Floppy Drive 0.2A CD ROM Drive 0.2A
Mother Board 1.5A DDR Memory 8.5A
Xeon 2.4HHz, 2X 14A@12V
Power Conversion Flowchart for a Typical Data Center

## Efficiency Assumptions
Server Power Supply Efficiency Profiles
| 0% | 10% | 20% | 30% | 50% | 75% | 100% | Menu Choice
Typical Case | 57.42% | 57.42% | 67.72% | 71.9% | 74.56% | 74.16% | 72.49% | No
High Efficiency Case | 69.7% | 69.7% | 76.77% | 78.97% | 81.81% | 81.72% | 80.72% | Yes
UPS Efficiency Profiles
| 0% | 10% | 20% | 30% | 50% | 75% | 100%
Do not evaluate UPS efficiency | 74% | 74% | 81% | 84% | 85% | 86% | 86%
High Efficiency Double Conversion | 87% | 87% | 93.1% | 93.8% | 94.1% | 94.5% | 94.8%
High Efficiency Delta Conversion | 87.72% | 87.72% | 93.35% | 95.22% | 96.67% | 96.93% | 97.09%
High Efficiency Flywheel | 89.48% | 89.48% | 92.88% | 95.02% | 97.01% | 97.75% | 97.83%
Redundancy Configuration Load Sharing Assumptions
|  | UPS Load Sharing | Power Supply Load Sharing
|  | 1 | 2
N |  | 1 | 1
Isolated Redundant |  | 1 | 1
N + 1 |  | 2 | 1
2N |  | 2 | 2
2(N+1) |  | 4 | 2
DC/DC VRM Efficiency |  | 1 |  | Menu Choice
Typical Case |  | 84% |  | No
High Efficiency Case |  | 92% |  | Yes
Power Budget for 1U Dual-Processor Server
|  | Typical (W) | Maximum (W)
Dual Processor Power (@1.75V DC) |  | 60 | 130
Mother Board, PCI Card, DDR Memory and Other Peripheral DC Power Consumption (@12V, 5V and 3.3V DC) |  | 60 | 220
Duty cycle (% time spent at "typical" or "maximum" power levels |  | 95% | 5%
Note on A12: Based on 4th order polynomial best fit of flywheel data.
Note on A9: Equivalent to average double conversion performance.
Note on A31: Based on measured load duration curves for servers.
Note on A4: Based on average values of measured power supplies.
Note on A5: Based on 95th percentile values of measured power supplies.
Note on A10: Best measured efficiency curve for double-conversion UPS.
Note on A11: Measured efficiency for delta conversion line-interactive UPS.